## DATASHEET
AUTOMATION DATA SHEET
PROJECT/CLIENT |  | 7 Generations
SITE LOCATION |  | 07-11-064-04 W6M KARR Gas Plant Grande Prairie
HARWARE CONFIGURATION
ANALYZER |  |  | CTX |  |  | 40-AIT-124
PLC |  |  | MICRO850
HMI |  |  | 5" PROFACE
STREAM 1 |  | TAG | 40-AIT-400 |  | PROCESS |  | Condy
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  | kPag | 0
[5 empty] | HIGH RANGE |  | 2000 |  | kPag | 7000 | psig | 400 | 60
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | -20 |  | C |  |  | 1850 | 264.2857
[5 empty] | HIGH RANGE |  | 100 |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | SWITCH |  | INTERRUPTION VALVE |  | PNUEMATIC
STREAM 2 |  | TAG | 50-AIT-400 |  | PROCESS |  | Condy
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  |  | 0
[5 empty] | HIGH RANGE |  | 2000 |  | kPag | 7000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | -20 |  | C
[5 empty] | HIGH RANGE |  | 100 |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | SWITCH |  | INTERRUPTION VALVE |  | PNUEMATIC
STREAM 3 |  | TAG | 60-AIT-400 |  | PROCESS |  | Condy
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  |  | 0
[5 empty] | HIGH RANGE |  | 2000 |  | kPag | 7000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | -20
[5 empty] | HIGH RANGE |  | 100 |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | N/A |  | INTERRUPTION VALVE |  | PNUEMATIC
STREAM 4 |  | TAG | N/A |  | PROCESS |  | N/A
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  |  | 0
[5 empty] | HIGH RANGE |  |  |  | kPag | 1000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE
[5 empty] | HIGH RANGE |  |  |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | N/A |  | INTERRUPTION VALVE |  | N/A
SOFTWARE CONFIGURATION
COMMUNICATION |  |  | TCP/IP MODBUS
OUTPUTS |  |  | 3 | QTY | Interrupt Valve
|  |  | 3 | QTY | Deemed C4 ( 0-10%)
COMPONENTS
| STREAM 1 | TAG | 40-AIT-400 |  |  | STREAM 2 | TAG | 50-AIT-400
| PROCESS | Condy |  |  |  | PROCESS | Condy
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
| STREAM 3 | TAG | 60-AIT-400 |  |  | STREAM 4 | TAG | N/A
| PROCESS | Condy |  |  |  | PROCESS | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
LOOKUP TABLES FOR DROP DOWNS
TRANSMITTER | CTX | MOL% | RTD |  | SWITCH |  | SWITCH
SENSOR | SSL | VOL% | TRANSMITTER |  | TRANSMITTER |  | AUTO
N/A | N/A | N/A | N/A |  | N/A |  | N/A
ELECTRIC |  | MICRO850 |  | 5" PROFACE |  |  | TCP/IP MODBUS
PNUEMATIC |  | MICRO820 |  | 7" PANELVIEW 800 |  |  | RS-485 MODBUS
N/A |  | N/A |  | 10" REDLION |  |  | RS-232 MODBUS
N/A
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
DO
AO

## IO MAP
7GENS - KARR GASS PLANT - IO MAP
DI | DESCRIPTION | STREAM | CHECKED | DO | DESCRIPTION | TAG | CHECKED
00 | SWITCH P2 | 40-AIT-400 |  | 00 | SPECTROMETER POWER | SPEC
01 | SWITCH P3 | 40-AIT-400 |  | 01 | SPARE
02 | SWITCH P2 | 50-AIT-400 |  | 02 | SPARE
03 | SWITCH P3 | 50-AIT-400 |  | 03 | SPARE
04 | SWITCH P2 | 60-AIT-400 |  | 04 | SPARE
05 | SWITCH P3 | 60-AIT-400 |  | 05 | SPARE
06 | SPARE |  |  | 07 | SPARE
07 | SPARE |  |  | 08 | VCON READY LIGHT | 40-UAL-400
08 | FSL | 40-FLS-400 |  | 09 | INTERRUPT SOLENOID | 40-EY-400
09 | SPARE |  |  | 10 | SPARE
10 | FLS | 50-FSL-400 |  | 11 | VCON READY LIGHT | 50-UAL-400
11 | SPARE |  |  | 12 | INTERRUPT SOLENOID | 50-EY-400
12 | FLS | 60-FLS-400 |  | 13 | SPARE
13 | SPARE |  |  | 14 | VCON READY LIGHT | 60-UAL-400
14 | SPARE |  |  | 15 | INTERRUPT SOLENOID | 60-EY-400
15 | SPARE |  |  | 16 | SPARE
|  |  |  | 17 | SPARE
|  |  |  | 18 | SPARE
AI | DESCRIPTION | TAG | CHECKED | AO | DESCRIPTION | STREAM | CHECKED
P2AI00 | PRESSURE | 40-PIT-400 |  | P4AO-00 | DEEMED C4 | 40-AIT-400
P2AI01 | PRESSURE | 50-PIT-400 |  | P4A0-01 | DEEMED C4 | 50-AIT-400
P2AI02 | SPARE |  |  | P5AO-00 | DEEMED C4 | 60-AIT-400
P2AI03 | PRESSURE | 60-PIT-400 |  | P5AO-01 | SPARE
P3AI00 | TEMPERATURE | 40-TIT-400
P3AI01 | SPARE
P3AI02 | TEMPERATURE | 60-TIT-400
P2AI03 | SPARE

## CLIENT MODBUS MAP
| 7 GENERATIONS - KARR GAS PLANT - CLIENT MODBUS MAP - INITIAL DRAFT 20082020 | [12 empty] | REV 0
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
1 | RESET | RESET | Reset Alarm | BOOL | WRITE | 00001 | N/A | N/A | N/A | N/A | OFF | RESET | Pulse for 2 seconds to reset latched alarms
2 | OBC_COMM_FAIL | OBC_COMM_FAIL | On Board Computer Communication Fault | BOOL | READ | 00002 | N/A | N/A | N/A | N/A | FAULT | OK | No change in VCON BeatModbus > 10 min
3 | SYSTEM_STATUS | SYSTEM_STATUS | Active Alarm on one or more streams | BOOL | READ | 00003 | N/A | N/A | N/A | N/A | FAULT | OK | No change in VCON BeatModbus > 10 min
4 | STREAM - 1 - CONDENSATE
5 | 40-UA_400A | Stream_1_Analyzer_Warning | Stream 1-Analyzer Common Warning Alarm | BOOL | READ | 00010 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
6 | 40-UA_400B | Stream_1_Model_Warning | Stream 1 - Analyzer Model Quality Warning | BOOL | READ | 00011 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
7 | 40-UA_400C | Stream_1_Sample_Panel_Warning | Stream 1-Sample Panel Common Warning Alarm | BOOL | READ | 00012 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
8 | 40-FSL_400 | Stream_1_FSL_COND | Stream 1 - Low Sample Flow Warning | BOOL | READ | 00013 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
9 | 40-PAH-400 | Stream_1_High_Pressure_Alarm | Stream 1 - High Pressure Warning Alarm | BOOL | READ | 00015 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
10 | 40-TAH-400 | Stream_1_High_Temperature_Alarm | Stream 1 - High Temperature Warning Alarm | BOOL | READ | 00016 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
11 | 40-XA_400A | Stream_1_Analyzer_Fault | Stream 1-Analyzer Common Fault Alarm | BOOL | READ | 00018 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
12 | 40-XA_400B | Stream_1_Model_Fault | Stream 1 - Analyzer Model Quality Fault | BOOL | READ | 00019 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
13 | 40-XA_400C | Stream_1_Sample_Panel_Fault | Stream 1-Sample Panel Common Fault Alarm | BOOL | READ | 00020 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
14
15 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
16 | STREAM - 2 - CONDENSATE
17 | 50-UA_400A | Stream_2_Analyzer_Warning | Stream 2-Analyzer Common Warning Alarm | BOOL | READ | 00050 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
18 | 50-UA_400B | Stream_2_Model_Warning | Stream 2 - Analyzer Model Quality Warning | BOOL | READ | 00051 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
19 | 50-UA_400C | Stream_2_Sample_Panel_Warning | Stream 2-Sample Panel Common Warning Alarm | BOOL | READ | 00052 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
20 | 50-FSL_400 | Stream_2_FSL_COND | Stream 2 - Low Sample Flow Warning | REAL | READ | 00053 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
21 | 50-PAH-400 | Stream_2_High_Pressure_Alarm | Stream 2 - High Pressure Warning Alarm | BOOL | READ | 00055 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
22 | 50-TAH-400 | Stream_2_High_Temperature_Alarm | Stream 2 - High Temperature Warning Alarm | BOOL | READ | 00056 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
23 | 50-XA_400A | Stream_2_Analyzer_Fault | Stream 2-Analyzer Common Fault Alarm | BOOL | READ | 00058 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
24 | 50-XA_400B | Stream_2_Model_Fault | Stream 2 - Analyzer Model Quality Fault | BOOL | READ | 00059 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
25 | 50-XA_400C | Stream_2_Sample_Panel_Fault | Stream 2-Sample Panel Common Fault Alarm | BOOL | READ | 00060 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
26
27 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
28 | STREAM - 3 - CONDENSATE
29 | 60-UA_400A | Stream_3_Analyzer_Warning | Stream 3-Analyzer Common Warning Alarm | BOOL | READ | 00090 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
30 | 60-UA_400B | Stream_3_Model_Warning | Stream 3 - Analyzer Model Quality Warning | BOOL | READ | 00091 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
31 | 60-UA_400C | Stream_3_Sample_Panel_Warning | Stream 3-Sample Panel Common Warning Alarm | BOOL | READ | 00092 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
32 | 60-FSL_400 | Stream_3_FSL_COND | Stream 3 - Low Sample Flow Warning | BOOL | READ | 00093 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
33 | 60-PAH-400 | Stream_3_High_Pressure_Alarm | Stream 3 - High Pressure Warning Alarm | BOOL | READ | 00095 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
34 | 60-TAH-400 | Stream_3_High_Temperature_Alarm | Stream 3 - High Temperature Warning Alarm | BOOL | READ | 00096 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
35 | 60-XA_400A | Stream_3_Analyzer_Fault | Stream 3-Analyzer Common Fault Alarm | BOOL | READ | 00098 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
36 | 60-XA_400B | Stream_3_Model_Fault | Stream 3 - Analyzer Model Quality Fault | BOOL | READ | 00099 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
37 | 60-XA_400C | Stream_3_Sample_Panel_Fault | Stream 3-Sample Panel Common Fault Alarm | BOOL | READ | 00100 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
38
39 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
40 | Holding Registers
41 | PLC_YEAR | PLC_YEAR | PLC Clock Year | INT | READ | 40001 |  | 2016 | 2116 |  |  |  | Real Time Clock From PLC
42 | PLC_MONTH | PLC_MONTH | PLC Clock Month | INT | READ | 40002 |  | 1 | 12 |  |  |  | Real Time Clock From PLC
43 | PLC_DAY | PLC_DAY | PLC Clock Day | INT | READ | 40003 |  | 1 | 31 |  |  |  | Real Time Clock From PLC
44 | PLC_HOUR | PLC_HOUR | PLC Clock Hour | INT | READ | 40004 |  | 0 | 24 |  |  |  | Real Time Clock From PLC
45 | PLC_MINUTE | PLC_MINUTE | PLC Clock Minute | INT | READ | 40005 |  | 0 | 60 |  |  |  | Real Time Clock From PLC
46 | PLC_SECOND | PLC_SECOND | PLC Clock Second | INT | READ | 40006 |  | 0 | 60 |  |  |  | Real Time Clock From PLC
47 | CT-4000 | CT_4000 | Communications Heartbeat Register to DCS | INT | READ | 40007 | N/A | 0 | 60 | N/A | N/A | N/A | PLC Clock Seconds passed onto master controller. Alarm if value has not changed after set time.
48 |  | STREAMS_ENABLED | Number of Streams Enabled in Logic | INT | READ | 40008 | N/A | 0 | 4 | N/A | N/A | N/A | Configuration Parameter
49
50 | STREAM - 1 - CONDENSATE
51 | 40-PIT-400 | Stream_1_Pressure | Stream 1, Pressure | REAL | READ | 40010 | N/A | 0 | 5000 | kPag | N/A | N/A
52 | 40-TIT-400 | Stream_1_Temperature | Stream 1, Temperature | REAL | READ | 40012 | N/A | -20 | 80 | C | N/A | N/A
53 | 40-AIT-400A | Stream_1_Deemed C4 | Stream 1, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40014 | N/A | 0 | 100 | VOL% | N/A | N/A
54 | 40-AIT-400A | Stream_1_C1 (Mol%) | Stream 1, C1 | REAL | READ | 40016 | N/A | 0 | 100 | MOL% | N/A | N/A
55 | 40-AIT-400B | Stream_1_C2 (Mol%) | Stream 1, C2 | REAL | READ | 40018 | N/A | 0 | 100 | MOL% | N/A | N/A
56 | 40-AIT-400C | Stream_1_C3 (Mol%) | Stream 1, C3 | REAL | READ | 40020 | N/A | 0 | 100 | MOL% | N/A | N/A
57 | 40-AIT-400D | Stream_1_iC4 (Mol%) | Stream 1, iC4 | REAL | READ | 40022 | N/A | 0 | 100 | MOL% | N/A | N/A
58 | 40-AIT-400E | Stream_1_nC4 (Mol%) | Stream 1, nC4 | REAL | READ | 40024 | N/A | 0 | 100 | MOL% | N/A | N/A
59 | 40-AIT-400J | Stream_1_Transmission | Stream 1, Transmission | REAL | READ | 40026 | N/A | 0 | 100 | % | N/A | N/A
60
61 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
62 | STREAM - 2 - CONDENSATE
63 | 50-PIT-400 | Stream_2_Pressure_1 | Stream 2, Pressure | REAL | READ | 40060 | N/A | 0 | 2000 | kPag | N/A | N/A
64 | 50-TIT-400 | Stream_2_Temperature_1 | Stream 2, Temperature | REAL | READ | 40062 | N/A | -20 | 80 | C | N/A | N/A
65 | 50-AIT-400A | Stream_2_Deemed C4 | Stream 2, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40064 | N/A | 0 | 100 | VOL% | N/A | N/A
66 | 50-AIT-400C | Stream_2_C1 (Vol%) | Stream 2, C1 | REAL | READ | 40066 | N/A | 0 | 100 | VOL% | N/A | N/A
67 | 50-AIT-400D | Stream_2_C2 (Vol%) | Stream 2, C2 | REAL | READ | 40068 | N/A | 0 | 100 | VOL% | N/A | N/A
68 | 50-AIT-400E | Stream_2_C3 (Vol%) | Stream 2, C3 | REAL | READ | 40070 | N/A | 0 | 100 | VOL% | N/A | N/A
69 | 50-AIT-400F | Stream_2_iC4 (Vol%) | Stream 2, iC4 | REAL | READ | 40072 | N/A | 0 | 100 | VOL% | N/A | N/A
70 | 50-AIT-400G | Stream_2_nC4 (Vol%) | Stream 2, nC4 | REAL | READ | 40074 | N/A | 0 | 100 | VOL% | N/A | N/A
71 | 50-AIT-400H | Stream_2_Stream_2_Transmission | Stream 2, Transmission | REAL | READ | 40076 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal
72
73 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
74 | STREAM - 3 - CONDENSATE
75 | 60-PIT-400 | Stream_3_Pressure_1 | Stream 3, Pressure | REAL | READ | 40110 | N/A | 0 | 2000 | kPag | N/A | N/A
76 | 60-TIT-400 | Stream_3_Temperature_1 | Stream 3, Temperature | REAL | READ | 40112 | N/A | -20 | 80 | C | N/A | N/A
77 | 60-AIT-400A | Stream_3_Deemed C4 | Stream 3, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40114 | N/A | 0 | 100 | VOL% | N/A | N/A
78 | 60-AIT-400C | Stream_3_C1 (Vol%) | Stream 3, C1 | REAL | READ | 40116 | N/A | 0 | 100 | VOL% | N/A | N/A
79 | 60-AIT-400D | Stream_3_C2 (Vol%) | Stream 3, C2 | REAL | READ | 40118 | N/A | 0 | 100 | VOL% | N/A | N/A
80 | 60-AIT-400E | Stream_3_C3 (Vol%) | Stream 3, C3 | REAL | READ | 40120 | N/A | 0 | 100 | VOL% | N/A | N/A
81 | 60-AIT-400F | Stream_3_iC4 (Vol%) | Stream 3, iC4 | REAL | READ | 40122 | N/A | 0 | 100 | VOL% | N/A | N/A
82 | 60-AIT-400G | Stream_3_nC4 (Vol%) | Stream 3, nC4 | REAL | READ | 40124 | N/A | 0 | 100 | VOL% | N/A | N/A
83 | 60-AIT-400H | Stream_3_Stream_3_Transmission | Stream 3, Transmission | REAL | READ | 40126 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal
84

## MASTER MODBUS MAP
| 7 GENERATIONS - KARR GAS PLANT - CLIENT MODBUS MAP - INITIAL DRAFT 20082020 | [12 empty] | REV 1
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
1 | RESET | RESET | Reset Alarm | BOOL | WRITE | 00001 | N/A | N/A | N/A | N/A | OFF | RESET | Pulse for 2 seconds to reset latched alarms
2 | OBC_COMM_FAIL | OBC_COMM_FAIL | On Board Computer Communication Fault | BOOL | READ | 00002 | N/A | N/A | N/A | N/A | FAULT | OK | No change in VCON BeatModbus > 10 min
3 | SYSTEM_STATUS | SYSTEM_STATUS | Active Alarm on one or more streams | BOOL | READ | 00003 | N/A | N/A | N/A | N/A | FAULT | OK | No change in VCON BeatModbus > 10 min
4 | STREAM - 1 - CONDENSATE
5 | 40-UA_400A | Stream_1_Analyzer_Warning | Stream 1-Analyzer Common Warning Alarm | BOOL | READ | 00010 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
6 | 40-UA_400B | Stream_1_Model_Warning | Stream 1 - Analyzer Model Quality Warning | BOOL | READ | 00011 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
7 | 40-UA_400C | Stream_1_Sample_Panel_Warning | Stream 1-Sample Panel Common Warning Alarm | BOOL | READ | 00012 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
8 | 40-FSL_400 | Stream_1_FSL_COND | Stream 1 - Low Sample Flow Warning | BOOL | READ | 00013 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
9 | 40-PAH-400 | Stream_1_High_Pressure_Alarm | Stream 1 - High Pressure Warning Alarm | BOOL | READ | 00015 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
10 | 40-TAH-400 | Stream_1_High_Temperature_Alarm | Stream 1 - High Temperature Warning Alarm | BOOL | READ | 00016 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
11 |  | Stream_1_Sampling_Alarm | Stream 1 - Sample Switch Warning | BOOL | READ | 00017 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
12 | 40-XA_400A | Stream_1_Analyzer_Fault | Stream 1-Analyzer Common Fault Alarm | BOOL | READ | 00018 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
13 | 40-XA_400B | Stream_1_Model_Fault | Stream 1 - Analyzer Model Quality Fault | BOOL | READ | 00019 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
14 | 40-XA_400C | Stream_1_Sample_Panel_Fault | Stream 1-Sample Panel Common Fault Alarm | BOOL | READ | 00020 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
15 |  | Stream_1_Temperature_Fault | Stream 1 - Temperature Transmitter Fault | BOOL | READ | 00021 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
16 |  | Stream_1_Pressure_Fault | Stream 1 - Pressure Transmitter Fault | BOOL | READ | 00022 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
17 |  | Stream_1_VCON_Normal | Stream 1 - Analyzer In Continous Analysis Mode | BOOL | READ | 00023 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
18 |  | Stream_1_VCON_Get_Ready | Stream 1 - Analyzer Sample Collection Mode Request | BOOL | READ | 00024 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
19 |  | Stream_1_VCON_Sampling | Stream 1 - Analyzer in Sample Collection Mode | BOOL | READ | 00025 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
20 |  | Stream_1_VCON_Ready | Stream 1 - Analyzer Ready For Sample Collection | BOOL | READ | 00026 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
21 |  | Stream_1_Sample_Source | Stream 1 - Sample Request Source | BOOL | READ | 00027 | N/A | N/A | N/A | N/A | HMI | SWITCH | Hardware Configuration Setting
22 |  | Stream_1_Active_Alarm | Stream 1 - Active Alarm | BOOL | READ | 00028 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
23 |  | Stream_1_Analyzer_Warning_Test_Enable | Stream 1 Analyzer Warning Test Enable | BOOL | READ | 00029 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
24 |  | Stream_1_Analyzer_Warning_Test | Stream 1 Analyzer Warning Test | BOOL | READ | 00030 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
25 |  | Stream_1_Analyzer_Fault_Test_Enable | Stream 1 Analyzer Fault Test Enable | BOOL | READ | 00031 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
26 |  | Stream_1_Analyzer_Fault_Test | Stream 1 Analyzer Fault Test | BOOL | READ | 00032 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
27 |  | Stream_1_Model_Warning_Test_Enable | Stream 1 Model Warning Test Enable | BOOL | READ | 00033 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
28 |  | Stream_1_Model_Warning_Test | Stream 1 Model Warning Test | BOOL | READ | 00034 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
29 |  | Stream_1_Model_Fault_Test_Enable | Stream 1 Model Fault Test Enable | BOOL | READ | 00035 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
30 |  | Stream_1_Model_Fault_Test | Stream 1 Model Fault Test | BOOL | READ | 00036 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
31 |  | Stream_1_Sample_Plan_Test_Enable | Stream 1 Sample Plan Test Enable | BOOL | READ | 00037 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
32 |  | Stream_1_Sample_Plan_Test | Stream 1 Sample Plan Test | BOOL | READ | 00038 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
33 |  | Stream_1_Transmission_Test_Enable | Stream 1 Transmission Test Enable | BOOL | READ | 00039 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
34
35 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
36 | STREAM - 2 - CONDENSATE
37 | 50-UA_400A | Stream_2_Analyzer_Warning | Stream 2-Analyzer Common Warning Alarm | BOOL | READ | 00050 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
38 | 50-UA_400B | Stream_2_Model_Warning | Stream 2 - Analyzer Model Quality Warning | BOOL | READ | 00051 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
39 | 50-UA_400C | Stream_2_Sample_Panel_Warning | Stream 2-Sample Panel Common Warning Alarm | BOOL | READ | 00052 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
40 | 50-FSL_400 | Stream_2_FSL_COND | Stream 2 - Low Sample Flow Warning | REAL | READ | 00053 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
41 | 50-PAH-400 | Stream_2_High_Pressure_Alarm | Stream 2 - High Pressure Warning Alarm | BOOL | READ | 00055 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
42 | 50-TAH-400 | Stream_2_High_Temperature_Alarm | Stream 2 - High Temperature Warning Alarm | BOOL | READ | 00056 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
43 |  | Stream_2_Sampling_Alarm | 400 | BOOL | READ | 00057 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
44 | 50-XA_400A | Stream_2_Analyzer_Fault | Stream 2-Analyzer Common Fault Alarm | BOOL | READ | 00058 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
45 | 50-XA_400B | Stream_2_Model_Fault | Stream 2 - Analyzer Model Quality Fault | BOOL | READ | 00059 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
46 | 50-XA_400C | Stream_2_Sample_Panel_Fault | Stream 2-Sample Panel Common Fault Alarm | BOOL | READ | 00060 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
47 |  | SPARE | SPARE | BOOL | READ | 00061 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
48 |  | Stream_2_Temperature_Fault | Stream 2 - Temperature Transmitter Fault | BOOL | READ | 00062 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
49 |  | Stream_2_Pressure_Fault | Stream 2 - Pressure Transmitter Fault | BOOL | READ | 00063 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
50 |  | Stream_2_VCON_Normal | Stream 2 - Analyzer In Continous Analysis Mode | BOOL | READ | 00064 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
51 |  | Stream_2_VCON_Get_Ready | Stream 2 - Analyzer Sample Collection Mode Request | BOOL | READ | 00065 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
52 |  | Stream_2_VCON_Sampling | Stream 2 - Analyzer in Sample Collection Mode | BOOL | READ | 00066 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
53 |  | Stream_2_VCON_Ready | Stream 2 - Analyzer Ready For Sample Collection | BOOL | READ | 00067 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
54 |  | Stream_2_Sample_Source | Stream 2 - Sample Request Source | BOOL | READ | 00068 | N/A | N/A | N/A | N/A | HMI | SWITCH | Hardware Configuration Setting
55 |  | Stream_2_Active_Alarm | Stream 2 - Active Alarm | BOOL | READ | 00069 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
56 |  | Stream_2_Analyzer_Warning_Test_Enable | Stream 2 Analyzer Warning Test Enable | BOOL | READ | 00070 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
57 |  | Stream_2_Analyzer_Warning_Test | Stream 2 Analyzer Warning Test | BOOL | READ | 00071 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
58 |  | Stream_2_Analyzer_Fault_Test_Enable | Stream 2 Analyzer Fault Test Enable | BOOL | READ | 00072 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
59 |  | Stream_2_Analyzer_Fault_Test | Stream 2 Analyzer Fault Test | BOOL | READ | 00073 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
60 |  | Stream_2_Model_Warning_Test_Enable | Stream 2 Model Warning Test Enable | BOOL | READ | 00074 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
61 |  | Stream_2_Model_Warning_Test | Stream 2 Model Warning Test | BOOL | READ | 00075 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
62 |  | Stream_2_Model_Fault_Test_Enable | Stream 2 Model Fault Test Enable | BOOL | READ | 00076 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
63 |  | Stream_2_Model_Fault_Test | Stream 2 Model Fault Test | BOOL | READ | 00077 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
64 |  | Stream_2_Sample_Plan_Test_Enable | Stream 2 Sample Plan Test Enable | BOOL | READ | 00078 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
65 |  | Stream_2_Sample_Plan_Test | Stream 2 Sample Plan Test | BOOL | READ | 00079 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
66 |  | Stream_2_Transmission_Test_Enable | Stream 2 Transmission Test Enable | BOOL | READ | 00080 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
67
68 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
69 | STREAM - 3 - CONDENSATE
70 | 60-UA_400A | Stream_3_Analyzer_Warning | Stream 3-Analyzer Common Warning Alarm | BOOL | READ | 00090 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
71 | 60-UA_400B | Stream_3_Model_Warning | Stream 3 - Analyzer Model Quality Warning | BOOL | READ | 00091 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
72 | 60-UA_400C | Stream_3_Sample_Panel_Warning | Stream 3-Sample Panel Common Warning Alarm | BOOL | READ | 00092 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
73 | 60-FSL_400 | Stream_3_FSL_COND | Stream 3 - Low Sample Flow Warning | BOOL | READ | 00093 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
74 | 60-PAH-400 | Stream_3_High_Pressure_Alarm | Stream 3 - High Pressure Warning Alarm | BOOL | READ | 00095 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
75 | 60-TAH-400 | Stream_3_High_Temperature_Alarm | Stream 3 - High Temperature Warning Alarm | BOOL | READ | 00096 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
76 |  | Stream_3_Sampling_Alarm | Stream 3 - Sample Switch Warning | BOOL | READ | 00097 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
77 | 60-XA_400A | Stream_3_Analyzer_Fault | Stream 3-Analyzer Common Fault Alarm | BOOL | READ | 00098 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
78 | 60-XA_400B | Stream_3_Model_Fault | Stream 3 - Analyzer Model Quality Fault | BOOL | READ | 00099 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
79 | 60-XA_400C | Stream_3_Sample_Panel_Fault | Stream 3-Sample Panel Common Fault Alarm | BOOL | READ | 00100 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
80 |  | SPARE | SPARE | BOOL | READ | 00101 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
81 |  | Stream_3_Temperature_Fault | Stream 3 - Temperature Transmitter Fault | BOOL | READ | 00102 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
82 |  | Stream_3_Pressure_Fault | Stream 3 - Pressure Transmitter Fault | BOOL | READ | 00103 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
83 |  | Stream_3_VCON_Normal | Stream 3 - Analyzer In Continous Analysis Mode | BOOL | READ | 00104 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
84 |  | Stream_3_VCON_Get_Ready | Stream 3 - Analyzer Sample Collection Mode Request | BOOL | READ | 00105 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
85 |  | Stream_3_VCON_Sampling | Stream 3 - Analyzer in Sample Collection Mode | BOOL | READ | 00106 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
86 |  | Stream_3_VCON_Ready | Stream 3 - Analyzer Ready For Sample Collection | BOOL | READ | 00107 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
87 |  | Stream_3_Sample_Source | Stream 3 - Sample Request Source | BOOL | READ | 00108 | N/A | N/A | N/A | N/A | HMI | SWITCH | Hardware Configuration Setting
88 |  | Stream_3_Active_Alarm | Stream 3 - Active Alarm | BOOL | READ | 00109 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
89 |  | Stream_3_Analyzer_Warning_Test_Enable | Stream 3 Analyzer Warning Test Enable | BOOL | READ | 00110 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
90 |  | Stream_3_Analyzer_Warning_Test | Stream 3 Analyzer Warning Test | BOOL | READ | 00111 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
91 |  | Stream_3_Analyzer_Fault_Test_Enable | Stream 3 Analyzer Fault Test Enable | BOOL | READ | 00112 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
92 |  | Stream_3_Analyzer_Fault_Test | Stream 3 Analyzer Fault Test | BOOL | READ | 00113 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
93 |  | Stream_3_Model_Warning_Test_Enable | Stream 3 Model Warning Test Enable | BOOL | READ | 00114 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
94 |  | Stream_3_Model_Warning_Test | Stream 3 Model Warning Test | BOOL | READ | 00115 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
95 |  | Stream_3_Model_Fault_Test_Enable | Stream 3 Model Fault Test Enable | BOOL | READ | 00116 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
96 |  | Stream_3_Model_Fault_Test | Stream 3 Model Fault Test | BOOL | READ | 00117 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
97 |  | Stream_3_Sample_Plan_Test_Enable | Stream 3 Sample Plan Test Enable | BOOL | READ | 00118 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
98 |  | Stream_3_Sample_Plan_Test | Stream 3 Sample Plan Test | BOOL | READ | 00119 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
99 |  | Stream_3_Transmission_Test_Enable | Stream 3 Transmission Test Enable | BOOL | READ | 00120 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
100
101 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
102 | Holding Registers
103 | PLC_YEAR | PLC_YEAR | PLC Clock Year | INT | READ | 40001 |  | 2016 | 2116 |  |  |  | Real Time Clock From PLC
104 | PLC_MONTH | PLC_MONTH | PLC Clock Month | INT | READ | 40002 |  | 1 | 12 |  |  |  | Real Time Clock From PLC
105 | PLC_DAY | PLC_DAY | PLC Clock Day | INT | READ | 40003 |  | 1 | 31 |  |  |  | Real Time Clock From PLC
106 | PLC_HOUR | PLC_HOUR | PLC Clock Hour | INT | READ | 40004 |  | 0 | 24 |  |  |  | Real Time Clock From PLC
107 | PLC_MINUTE | PLC_MINUTE | PLC Clock Minute | INT | READ | 40005 |  | 0 | 60 |  |  |  | Real Time Clock From PLC
108 | PLC_SECOND | PLC_SECOND | PLC Clock Second | INT | READ | 40006 |  | 0 | 60 |  |  |  | Real Time Clock From PLC
109 | CT-4000 | CT_4000 | Communications Heartbeat Register to DCS | INT | READ | 40007 | N/A | 0 | 60 | N/A | N/A | N/A | PLC Clock Seconds passed onto master controller. Alarm if value has not changed after set time.
110 |  | STREAMS_ENABLED | Number of Streams Enabled in Logic | INT | READ | 40008 | N/A | 0 | 4 | N/A | N/A | N/A | Configuration Parameter
111
112 | STREAM - 1 - CONDENSATE
113 | 40-PIT-400 | Stream_1_Pressure | Stream 1, Pressure | REAL | READ | 40010 | N/A | 0 | 5000 | kPag | N/A | N/A
114 | 40-TIT-400 | Stream_1_Temperature | Stream 1, Temperature | REAL | READ | 40012 | N/A | -20 | 80 | C | N/A | N/A
115 | 40-AIT-400A | Stream_1_Deemed C4 | Stream 1, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40014 | N/A | 0 | 100 | VOL% | N/A | N/A
116 | 40-AIT-400A | Stream_1_C1 (Mol%) | Stream 1, C1 | REAL | READ | 40016 | N/A | 0 | 100 | MOL% | N/A | N/A
117 | 40-AIT-400B | Stream_1_C2 (Mol%) | Stream 1, C2 | REAL | READ | 40018 | N/A | 0 | 100 | MOL% | N/A | N/A
118 | 40-AIT-400C | Stream_1_C3 (Mol%) | Stream 1, C3 | REAL | READ | 40020 | N/A | 0 | 100 | MOL% | N/A | N/A
119 | 40-AIT-400D | Stream_1_iC4 (Mol%) | Stream 1, iC4 | REAL | READ | 40022 | N/A | 0 | 100 | MOL% | N/A | N/A
120 | 40-AIT-400E | Stream_1_nC4 (Mol%) | Stream 1, nC4 | REAL | READ | 40024 | N/A | 0 | 100 | MOL% | N/A | N/A
121 | 40-AIT-400J | Stream_1_Transmission | Stream 1, Transmission | REAL | READ | 40026 | N/A | 0 | 100 | % | N/A | N/A
122 |  | Stream_1_Sample_Mode | Stream 1, Sampling Mode | INT | READ | 40028 | N/A | 0 | 4 | N/A | N/A | N/A
123 |  | Stream_1_Sample_Mode_HMI_Select | Stream 1, Sampling Mode HMI Select | INT | READ | 40029 | N/A | 0 | 1 | N/A | N/A | N/A
124 |  | Stream_1_Pressure_Range_Lo | Stream 1, Cell Pressure Scale Low SP | REAL | READ | 40030 | N/A | 0 | 100 | kPag | N/A | N/A
125 |  | Stream_1_Pressure_Range_Hi | Stream 1, Cell Pressure Scale High SP | REAL | READ | 40032 | N/A | 0 | 100 | kPag | N/A | N/A
126 |  | Stream_1_Pressure_Alarm_Hi_SP | Stream 1, Cell Pressure Scale High Alarm SP | REAL | READ | 40034 | N/A | 0 | 100 | kPag | N/A | N/A
127 |  | Stream_1_Temperature_Range_Lo | Stream 1, Cell Temperature Scale Low SP | REAL | READ | 40036 | N/A | 0 | 300 | C | N/A | N/A
128 |  | Stream_1_Temperature_Range_Hi | Stream 1, Cell Temperature Scale High SP | REAL | READ | 40038 | N/A | 0 | 300 | C | N/A | N/A
129 |  | Stream_1_Temperature_Alarm_Hi_SP | Stream 1, Cell Temperature Scale High Alarm SP | REAL | READ | 40040 | N/A | 0 | 300 | C | N/A | N/A | Analyzer Diagnostic Signal
130 |  | Stream_1_Transmission_Test | Stream 1 Transmission Test | REAL | R/W | 40042 | N/A | 0 | 300 | % | N/A | N/A
131
132 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
133 | STREAM - 2 - CONDENSATE
134 | 50-PIT-400 | Stream_2_Pressure_1 | Stream 2, Pressure | REAL | READ | 40060 | N/A | 0 | 2000 | kPag | N/A | N/A
135 | 50-TIT-400 | Stream_2_Temperature_1 | Stream 2, Temperature | REAL | READ | 40062 | N/A | -20 | 80 | C | N/A | N/A
136 | 50-AIT-400A | Stream_2_Deemed C4 | Stream 2, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40064 | N/A | 0 | 100 | VOL% | N/A | N/A
137 | 50-AIT-400C | Stream_2_C1 (Vol%) | Stream 2, C1 | REAL | READ | 40066 | N/A | 0 | 100 | VOL% | N/A | N/A
138 | 50-AIT-400D | Stream_2_C2 (Vol%) | Stream 2, C2 | REAL | READ | 40068 | N/A | 0 | 100 | VOL% | N/A | N/A
139 | 50-AIT-400E | Stream_2_C3 (Vol%) | Stream 2, C3 | REAL | READ | 40070 | N/A | 0 | 100 | VOL% | N/A | N/A
140 | 50-AIT-400F | Stream_2_iC4 (Vol%) | Stream 2, iC4 | REAL | READ | 40072 | N/A | 0 | 100 | VOL% | N/A | N/A
141 | 50-AIT-400G | Stream_2_nC4 (Vol%) | Stream 2, nC4 | REAL | READ | 40074 | N/A | 0 | 100 | VOL% | N/A | N/A
142 | 50-AIT-400H | Stream_2_Stream_2_Transmission | Stream 2, Transmission | REAL | READ | 40076 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal
143 |  | Stream_2_Sample_Mode | Stream 2, Sampling Mode | INT | READ | 40078 | N/A | 0 | 3 | N/A | N/A | N/A | 0=Normal, 1=Get Ready, 2=Ready, 3=Sampling
144 |  | Stream_2_Sample_Mode_HMI_Select | Stream 2, Sampling Mode HMI Select | INT | R/W | 40079 | N/A | 0 | 2 | N/A | N/A | N/A | 1 = HMI P2, 2 = HMI P3
145 |  | Stream_2_Pressure_Range_Lo | Stream 2, Cell Pressure Scale Low SP | REAL | R/W | 40080 | N/A | 0 | 10000 | kpa | N/A | N/A
146 |  | Stream_2_Pressure_Range_Hi | Stream 2, Cell Pressure Scale High SP | REAL | R/W | 40082 | N/A | 0 | 10000 | kpa | N/A | N/A
147 |  | Stream_2_Pressure_Alarm_Hi_SP | Stream 2, Cell Pressure Scale High Alarm SP | REAL | R/W | 40084 | N/A | 0 | 10000 | kpa | N/A | N/A
148 |  | Stream_2_Temperature_Range_Lo | Stream 2, Cell Temperature Scale Low SP | REAL | R/W | 40086 | N/A | 0 | 300 | C | N/A | N/A
149 |  | Stream_2_Temperature_Range_Hi | Stream 2, Cell Temperature Scale High SP | REAL | R/W | 40088 | N/A | 0 | 300 | C | N/A | N/A
150 |  | Stream_2_Temperature_Alarm_Hi_SP | Stream 2, Cell Temperature Scale High Alarm SP | REAL | R/W | 40090 | N/A | 0 | 300 | C | N/A | N/A
151 |  | Stream_2_Transmission_Test | Stream 2 Transmission Test | REAL | R/W | 40092 | N/A | 0 | 100 | % | N/A | N/A
152
153 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
154 | STREAM - 3 - CONDENSATE
155 | 60-PIT-400 | Stream_3_Pressure_1 | Stream 3, Pressure | REAL | READ | 40110 | N/A | 0 | 2000 | kPag | N/A | N/A
156 | 60-TIT-400 | Stream_3_Temperature_1 | Stream 3, Temperature | REAL | READ | 40112 | N/A | -20 | 80 | C | N/A | N/A
157 | 60-AIT-400A | Stream_3_Deemed C4 | Stream 3, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40114 | N/A | 0 | 100 | VOL% | N/A | N/A
158 | 60-AIT-400C | Stream_3_C1 (Vol%) | Stream 3, C1 | REAL | READ | 40116 | N/A | 0 | 100 | VOL% | N/A | N/A
159 | 60-AIT-400D | Stream_3_C2 (Vol%) | Stream 3, C2 | REAL | READ | 40118 | N/A | 0 | 100 | VOL% | N/A | N/A
160 | 60-AIT-400E | Stream_3_C3 (Vol%) | Stream 3, C3 | REAL | READ | 40120 | N/A | 0 | 100 | VOL% | N/A | N/A
161 | 60-AIT-400F | Stream_3_iC4 (Vol%) | Stream 3, iC4 | REAL | READ | 40122 | N/A | 0 | 100 | VOL% | N/A | N/A
162 | 60-AIT-400G | Stream_3_nC4 (Vol%) | Stream 3, nC4 | REAL | READ | 40124 | N/A | 0 | 100 | VOL% | N/A | N/A
163 | 60-AIT-400H | Stream_3_Stream_3_Transmission | Stream 3, Transmission | REAL | READ | 40126 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal
164 |  | Stream_3_Sample_Mode | Stream 3, Sampling Mode | INT | READ | 40128 | N/A | 0 | 3 | N/A | N/A | N/A | 0=Normal, 1=Get Ready, 2=Ready, 3=Sampling
165 |  | Stream_3_Sample_Mode_HMI_Select | Stream 3, Sampling Mode HMI Select | INT | R/W | 40129 | N/A | 0 | 2 | N/A | N/A | N/A | 1 = HMI P2, 2 = HMI P3
166 |  | Stream_3_Pressure_Range_Lo | Stream 3, Cell Pressure Scale Low SP | REAL | R/W | 40130 | N/A | 0 | 10000 | kpa | N/A | N/A
167 |  | Stream_3_Pressure_Range_Hi | Stream 3, Cell Pressure Scale High SP | REAL | R/W | 40132 | N/A | 0 | 10000 | kpa | N/A | N/A
168 |  | Stream_3_Pressure_Alarm_Hi_SP | Stream 3, Cell Pressure Scale High Alarm SP | REAL | R/W | 40134 | N/A | 0 | 10000 | kpa | N/A | N/A
169 |  | Stream_3_Temperature_Range_Lo | Stream 3, Cell Temperature Scale Low SP | REAL | R/W | 40136 | N/A | 0 | 300 | C | N/A | N/A
170 |  | Stream_3_Temperature_Range_Hi | Stream 3, Cell Temperature Scale High SP | REAL | R/W | 40138 | N/A | 0 | 300 | C | N/A | N/A
171 |  | Stream_3_Temperature_Alarm_Hi_SP | Stream 3, Cell Temperature Scale High Alarm SP | REAL | R/W | 40140 | N/A | 0 | 300 | C | N/A | N/A
172 |  | Stream_3_Transmission_Test | Stream 3 Transmission Test | REAL | R/W | 40142 | N/A | 0 | 100 | % | N/A | N/A
173

## CONDY A1
40-AIT-400
SPECIES | REG TYPE | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1_MOL | Input | 7001 | 8001 | 32-bit Floating Point | VOL%
C2_MOL | Input | 7003 | 8003 | 32-bit Floating Point | VOL%
C3_MOL | Input | 7005 | 8005 | 32-bit Floating Point | VOL%
iC4_MOL | Input | 7007 | 8007 | 32-bit Floating Point | VOL%
nC4_MOL | Input | 7009 | 8009 | 32-bit Floating Point | VOL%
DEEMED C4 | Input | 7011 | 8011 | 32-bit Floating Point | VOL%
Transmission_1 | Input | 7017 |  | 32-bit Floating Point | %
Fault_Ireg | Input | 7019 |  | 16-bit Integer | ENCODED
Warning_Ireg | Input | 7020 |  | 16-bit Integer | ENCODED
Flow Interrupt | Input | 7021 |  | 16-bit Integer | 41=Closed
Alarm IReg | Input | 7022 |  | 16-bit Integer | 0=Open, 41 = Closed
Model IReg | Input | 7023 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7024 |  | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7025 |  | 16-bit Integer | 41=Trigger to pull sample
INPUTS
Temperature_1 | Holding | 1 | N/A | 16-bit Integer
Pressure_1 | Holding | 2 | N/A | 16-bit Integer
vcon trigger | Holding | 3 | N/A | 16-bit Integer
no flow | Holding | 4 | N/A | 16-bit Integer
vcon_get_ready | Holding | 21 | N/A | 16-bit Integer | 41=VCON GET READY
vcon_sample | Holding | 22 | N/A | 16-bit Integer | 41=SAMPLE IN PROGRESS
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer | REMOTE POWER CYCLE
Status_Modbus | Input | 7097 | N/A | 16-bit Integer | STREAM INDICATOR
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer | TOGGLE BETWENN 0 AND 41
prefix:

## CONDY A2
50-AIT-400
SPECIES | REG TYPE | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1_VOL | Input | 7101 | 8101 | 32-bit Floating Point | VOL%
C2_VOL | Input | 7103 | 8103 | 32-bit Floating Point | VOL%
C3_VOL | Input | 7105 | 8105 | 32-bit Floating Point | VOL%
iC4_VOL | Input | 7107 | 8107 | 32-bit Floating Point | VOL%
nC4_VOL | Input | 7109 | 8109 | 32-bit Floating Point | VOL%
DEEMED_C4 | Input | 7111 | 8111 | 32-bit Floating Point | VOL%
Transmission_1 | Input | 7117 |  | 32-bit Floating Point | %
Fault_Ireg | Input | 7119 |  | 16-bit Integer | ENCODED
Warning_Ireg | Input | 7120 |  | 16-bit Integer | ENCODED
Flow Interrupt | Input | 7121 |  | 16-bit Integer | 41=Closed
Alarm IReg | Input | 7122 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
Model IReg | Input | 7123 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7124 |  | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7125 |  | 16-bit Integer | 41=Trigger to pull sample
INPUTS
Temperature_1 | Holding | 5 | N/A | 16-bit Integer
Pressure_1 | Holding | 6 | N/A | 16-bit Integer
vcon trigger | Holding | 7 | N/A | 16-bit Integer
no flow | Holding | 8 | N/A | 16-bit Integer
vcon_get_ready | Holding | 23 | N/A | 16-bit Integer | 41=VCON GET READY
vcon_sample | Holding | 24 | N/A | 16-bit Integer | 41=SAMPLE IN PROGRESS
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer | REMOTE POWER CYCLE
Status_Modbus | Input | 7097 | N/A | 16-bit Integer | STREAM INDICATOR
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer | TOGGLE BETWENN 0 AND 41

## CONDY A3
60-AIT-400
SPECIES | REG TYPE | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1_VOL | Input | 7201 | 8201 | 32-bit Floating Point | VOL%
C2_VOL | Input | 7203 | 8203 | 32-bit Floating Point | VOL%
C3_VOL | Input | 7205 | 8205 | 32-bit Floating Point | VOL%
iC4_VOL | Input | 7207 | 8207 | 32-bit Floating Point | VOL%
nC4_VOL | Input | 7209 | 8209 | 32-bit Floating Point | VOL%
DEEMED_C4 | Input | 7211 | 8211 | 32-bit Floating Point | VOL%
Transmission_1 | Input | 7217 |  | 32-bit Floating Point | %
Fault_Ireg | Input | 7219 |  | 16-bit Integer | ENCODED
Warning_Ireg | Input | 7220 |  | 16-bit Integer | ENCODED
Flow Interrupt | Input | 7221 |  | 16-bit Integer | 41=Closed
Alarm IReg | Input | 7222 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
Model IReg | Input | 7223 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7224 |  | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7225 |  | 16-bit Integer | 41=Trigger to pull sample
INPUTS
Temperature_1 | Holding | 9 | N/A | 16-bit Integer
Pressure_1 | Holding | 10 | N/A | 16-bit Integer
vcon trigger | Holding | 11 | N/A | 16-bit Integer
no flow | Holding | 12 | N/A | 16-bit Integer
vcon_get_ready | Holding | 25 | N/A | 16-bit Integer | 41=VCON GET READY
vcon_sample | Holding | 26 | N/A | 16-bit Integer | 41=SAMPLE IN PROGRESS
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer | REMOTE POWER CYCLE
Status_Modbus | Input | 7097 | N/A | 16-bit Integer | STREAM INDICATOR
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer | TOGGLE BETWENN 0 AND 41

## CHANGE LOG
DATE | CHANGES | BY
2020-12-08 | INITIAL DRAFT | DD

## DataTypes (hidden)
Data Type | Description
BOOL | Boolean, Single bit
WORD | Unsigned 16 bit value bit 0 is the low bit bit 15 is the high bit
SHORT | Signed 16 bit value bit 0 is the low bit bit 14 is the high bit bit 15 is the sign bit
DWORD | Unsigned 32 bit value bit 0 is the low bit bit 31 is the high bit
LONG | Signed 32 bit value bit 0 is the low bit bit 30 is the high bit bit 31 is the sign bit
BCD | Two byte packed BCD Value range is 0-9999. Behavior is undefined for values beyond this range.
LBCD | Four byte packed BCD Value range is 0-99999999. Behavior is undefined for values beyond this range.
STRING | Null terminated ASCII string Supported on Modbus Model, includes Hi-Lo Lo-Hi byte order selection.
DOUBLE (Note 1) | 64 bit floating point value The driver interprets four consecutive registers as a double precision value by making the last two registers the high DWord and the first two registers the low DWord.
DOUBLE Example | If register 40001 is specified as a double, bit 0 of register 40001 would be bit 0 of the 64 bit data type and bit 15 of register 40004 would be bit 63 of the 64 bit data type.
FLOAT (Note 1) | 32 bit floating point value The driver interprets two consecutive registers as a single precision value by making the last register the high word and the first register the low word.
FLOAT Example | If register 40001 is specified as a float, bit 0 of register 40001 would be bit 0 of the 32 bit data type and bit 15 of register 40002 would be bit 31 of the 32 bit data type.
Notes:
1. The descriptions assume the default; that is, first DWord low data handling of 64 bit data types and first word
low data handling of 32 bit data types.
2. Standard data format names have been selected. If other names are desired, specify the bytes and range.