## DATASHEET
AUTOMATION DATA SHEET
PROJECT/CLIENT |  | 7 Generations
SITE LOCATION |  | 07-11-064-04 W6M KARR Gas Plant Grande Prairie
HARWARE CONFIGURATION
ANALYZER |  |  | CTX |  | 40-AIT-124
PLC |  |  | MICRO850
HMI |  |  | 5" PROFACE
STREAM 1 |  | TAG | 40AIT-400 |  | PROCESS |  | Condy
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  | kPag | 0
[5 empty] | HIGH RANGE |  | 10000 |  | kPag | 7000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | -20 |  | C
[5 empty] | HIGH RANGE |  | 110 |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | SWITCH |  | INTERRUPTION VALVE |  | PNUEMATIC
STREAM 2 |  | TAG | 50-AIT-400 |  | PROCESS |  | Condy
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  |  | 0
[5 empty] | HIGH RANGE |  | 10000 |  | kPag | 7000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | -20 |  | C
[5 empty] | HIGH RANGE |  | 110 |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | SWITCH |  | INTERRUPTION VALVE |  | PNUEMATIC
STREAM 3 |  | TAG | 60-AIT-400 |  | PROCESS |  | Condy
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  |  | 0
[5 empty] | HIGH RANGE |  | 10000 |  | kPag | 7000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | -20
[5 empty] | HIGH RANGE |  | 110 |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | N/A |  | INTERRUPTION VALVE |  | PNUEMATIC
STREAM 4 |  | TAG |  |  | PROCESS
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  |  | 0
[5 empty] | HIGH RANGE |  |  |  | kPag | 1000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE
[5 empty] | HIGH RANGE |  |  |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | N/A |  | INTERRUPTION VALVE |  | N/A
SOFTWARE CONFIGURATION
COMMUNICATION |  |  | TCP/IP MODBUS
OUTPUTS |  |  | 3 | QTY | Interrupt Valve
|  |  | 3 | QTY | Deemed C4
COMPONENTS
| STREAM 1 | TAG | 40AIT-400 |  |  | STREAM 2 | TAG | 50-AIT-400
| PROCESS | Condy |  |  |  | PROCESS | Condy
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
| STREAM 3 | TAG | 60-AIT-400 |  |  | STREAM 4 | TAG
| PROCESS | Condy |  |  |  | PROCESS | 0
|  |  |  | VOL% |  |  |  |  | MOL%
|  |  |  | VOL% |  |  |  |  | MOL%
|  |  |  | VOL% |  |  |  |  | MOL%
|  |  |  | VOL% |  |  |  |  | MOL%
|  |  |  | VOL% |  |  |  |  | MOL%
|  |  |  | VOL% |  |  |  |  | MOL%
|  |  |  | VOL% |  |  |  |  | MOL%
|  |  |  | VOL% |  |  |  |  | MOL%
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
LOOKUP TABLES FOR DROP DOWNS
TRANSMITTER | CTX | MOL% | RTD |  | SWITCH |  | SWITCH
SENSOR | SSL | VOL% | TRANSMITTER |  | TRANSMITTER |  | AUTO
N/A | N/A | N/A | N/A |  | N/A |  | N/A
ELECTRIC |  | MICRO850 |  | 5" PROFACE |  |  | TCP/IP MODBUS
PNUEMATIC |  | MICRO820 |  | 7" PANELVIEW 800 |  |  | RS-485 MODBUS
N/A |  | N/A |  | 10" REDLION |  |  | RS-232 MODBUS
N/A
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
DO
AO

## CLIENT_Datamap
| PETRONAS - TOWN NORTH - CLIENT MODBUS MAP - FAT 2020/07/16 | [12 empty] | REV 1
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | VERIFIED BY
1 | RESET | RESET | Reset Alarm | BOOL | WRITE | 00001 | N/A | N/A | N/A | N/A | OFF | RESET | Pulse for 2 seconds to reset latched alarms | DD/JW - 20/07/16
2 | OBC_COMM_FAIL | OBC_COMM_FAIL | On Board Computer Communication Fault | BOOL | READ | 00002 | N/A | N/A | N/A | N/A | FAULT | OK | No change in VCON BeatModbus > 10 min | DD/JW - 20/07/16
3 | STREAM - 1 - LPG
4 | UA_4050A | Stream_1_Analyzer_Warning | Stream 1-Analyzer Common Warning Alarm | BOOL | READ | 00010 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet | DD/JW - 20/07/16
5 | UA_4050B | Stream_1_Model_Warning | Stream 1 - Analyzer Model Quality Warning | BOOL | READ | 00011 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality | DD/JW - 20/07/16
6 | UA_4050C | Stream_1_Sample_Panel_Warning | Stream 1-Sample Panel Common Warning Alarm | BOOL | READ | 00012 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure | DD/JW - 20/07/16
7 | PAH-4050 | Stream_1_High_Pressure_Alarm | Stream 1 - High Pressure Warning Alarm | BOOL | READ | 00015 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 20/07/16
8 | TAH-4050 | Stream_1_High_Temperature_Alarm | Stream 1 - High Temperature Warning Alarm | BOOL | READ | 00016 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 20/07/16
9 | XA_4050A | Stream_1_Analyzer_Fault | Stream 1-Analyzer Common Fault Alarm | BOOL | READ | 00018 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet | DD/JW - 20/07/16
10 | XA_4050B | Stream_1_Model_Fault | Stream 1 - Analyzer Model Quality Fault | BOOL | READ | 00019 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality | DD/JW - 20/07/16
11 | XA_4050C | Stream_1_Sample_Panel_Fault | Stream 1-Sample Panel Common Fault Alarm | BOOL | READ | 00020 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure | DD/JW - 20/07/16
12 | STREAM - 2 - DEBUTANIZER
13 | UA_4002A | Stream_2_Analyzer_Warning | Stream 2-Analyzer Common Warning Alarm | BOOL | READ | 00050 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet | DD/JW - 20/07/16
14 | UA_4002B | Stream_2_Model_Warning | Stream 2 - Analyzer Model Quality Warning | BOOL | READ | 00051 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality | DD/JW - 20/07/16
15 | UA-4002C | Stream_2_Sample_Panel_Warning | Stream 2-Sample Panel Common Warning Alarm | BOOL | READ | 00052 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure | DD/JW - 20/07/16
16 | PAH-4002 | Stream_2_High_Pressure_Alarm | Stream 2 - High Pressure Warning Alarm | BOOL | READ | 00055 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 20/07/16
17 | TAH-4002 | Stream_2_High_Temperature_Alarm | Stream 2 - High Temperature Warning Alarm | BOOL | READ | 00056 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 20/07/16
18 |  | Stream_2_Sampling_Alarm | Stream 2 - Sample Switch Warning | BOOL | READ | 00057 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min | DD/JW - 20/07/16
19 | XA-4002A | Stream_2_Analyzer_Fault | Stream 2-Analyzer Common Fault Alarm | BOOL | READ | 00058 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet | DD/JW - 20/07/16
20 | XA-4002B | Stream_2_Model_Fault | Stream 2 - Analyzer Model Quality Fault | BOOL | READ | 00059 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality | DD/JW - 20/07/16
21 | XA-4002C | Stream_2_Sample_Panel_Fault | Stream 2-Sample Panel Common Fault Alarm | BOOL | READ | 00060 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure | DD/JW - 20/07/16
22 | STREAM - 3 - STABILIZER
23 | UA_4003A | Stream_3_Analyzer_Warning | Stream 3-Analyzer Common Warning Alarm | BOOL | READ | 00090 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet | DD/JW - 20/07/16
24 | UA_4003B | Stream_3_Model_Warning | Stream 3 - Analyzer Model Quality Warning | BOOL | READ | 00091 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality | DD/JW - 20/07/16
25 | UA-4003C | Stream_3_Sample_Panel_Warning | Stream 3-Sample Panel Common Warning Alarm | BOOL | READ | 00092 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure | DD/JW - 20/07/16
26 | PAH-4003 | Stream_3_High_Pressure_Alarm | Stream 3 - High Pressure Warning Alarm | BOOL | READ | 00095 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 20/07/16
27 | TAH-4003 | Stream_3_High_Temperature_Alarm | Stream 3 - High Temperature Warning Alarm | BOOL | READ | 00096 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 20/07/16
28 | XA-4003A | Stream_3_Analyzer_Fault | Stream 3-Analyzer Common Fault Alarm | BOOL | READ | 00098 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet | DD/JW - 20/07/16
29 | XA-4003B | Stream_3_Model_Fault | Stream 3 - Analyzer Model Quality Fault | BOOL | READ | 00099 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality | DD/JW - 20/07/16
30 | XA-4003C | Stream_3_Sample_Panel_Fault | Stream 3-Sample Panel Common Fault Alarm | BOOL | READ | 00100 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure | DD/JW - 20/07/16
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | VERIFIED BY
32 | CT-4000 | CT_4000 | Communications Heartbeat Register to DCS | INT | READ | 40007 | N/A | 0 | 60 | N/A | N/A | N/A | PLC Clock Seconds passed onto master controller. Alarm if value has not changed after set time. | DD/JW - 20/07/16
33 | STREAM - 1 - LPG
34 | PIT-4104 | Stream_1_Pressure | Stream 1, Pressure | REAL | READ | 40010 | N/A | 0 | 5000 | kPag | N/A | N/A |  | DD/JW - 20/07/16
35 | TIT-4050 | Stream_1_Temperature | Stream 1, Temperature | REAL | READ | 40012 | N/A | -20 | 80 | C | N/A | N/A |  | DD/JW - 20/07/16
36 | AIT-4050A | Stream_1_C1 (Mol%) | Stream 1, C1 | REAL | READ | 40014 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 20/07/16
37 | AIT-4050B | Stream_1_C2 (Mol%) | Stream 1, C2 | REAL | READ | 40016 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 20/07/16
38 | AIT-4050C | Stream_1_C3 (Mol%) | Stream 1, C3 | REAL | READ | 40018 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 20/07/16
39 | AIT-4050D | Stream_1_iC4 (Mol%) | Stream 1, iC4 | REAL | READ | 40020 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 20/07/16
40 | AIT-4050E | Stream_1_nC4 (Mol%) | Stream 1, nC4 | REAL | READ | 40022 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 20/07/16
41 | AIT-4050F | Stream_1_iC5 (Mol%) | Stream 1, iC5 | REAL | READ | 40024 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 20/07/16
42 | AIT-4050G | Stream_1_nC5 (Mol%) | Stream 1, nC5 | REAL | READ | 40026 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 20/07/16
43 | AIT-4050H | Stream_1_C6+ (Mol%) | Stream 1, C6 plus | REAL | READ | 40028 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 20/07/16
44 | AIT-4050J | Stream_1_Transmission | Stream 1, Transmission | REAL | READ | 40030 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal | DD/JW - 20/07/16
45 | STREAM - 2 - DEBUTANIZER
46 | PIT-4002 | Stream_2_Pressure_1 | Stream 2, Pressure | REAL | READ | 40060 | N/A | 0 | 2000 | kPag | N/A | N/A |  | DD/JW - 20/07/16
47 | TIT-4002 | Stream_2_Temperature_1 | Stream 2, Temperature | REAL | READ | 40062 | N/A | -20 | 80 | C | N/A | N/A |  | DD/JW - 20/07/16
48 | AIT-4002A | Stream_2_Deemed C4 | Stream 2, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40064 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
49 | AIT-4002B | Stream_2_VPCR | Stream 2, VAPOUR PRESSURE D6377 | REAL | READ | 40066 | N/A | 0 | 100 | kPaa | N/A | N/A | NOT USED ON THIS BUILD | N/A
50 | AIT-4002C | Stream_2_C1 (Vol%) | Stream 2, C1 | REAL | READ | 40068 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
51 | AIT-4002D | Stream_2_C2 (Vol%) | Stream 2, C2 | REAL | READ | 40070 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
52 | AIT-4002E | Stream_2_C3 (Vol%) | Stream 2, C3 | REAL | READ | 40072 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
53 | AIT-4002F | Stream_2_iC4 (Vol%) | Stream 2, iC4 | REAL | READ | 40074 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
54 | AIT-4002G | Stream_2_nC4 (Vol%) | Stream 2, nC4 | REAL | READ | 40076 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
55 | AIT-4002H | Stream_2_Stream_2_Transmission | Stream 2, Transmission | REAL | READ | 40078 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal | DD/JW - 20/07/16
56 | STREAM - 3 - STABILIZER
57 | PIT-4003 | Stream_3_Pressure_1 | Stream 3, Pressure | REAL | READ | 40100 | N/A | 0 | 2000 | kPag | N/A | N/A |  | DD/JW - 20/07/16
58 | TIT-4003 | Stream_3_Temperature_1 | Stream 3, Temperature | REAL | READ | 40102 | N/A | -20 | 80 | C | N/A | N/A |  | DD/JW - 20/07/16
59 | AIT-4003A | Stream_3_Deemed C4 | Stream 3, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40104 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
60 | AIT-4003B | Stream_3_VPCR | Stream 3, VAPOUR PRESSURE D6377 | REAL | READ | 40106 | N/A | 0 | 100 | kPa | N/A | N/A | NOT USED ON THIS BUILD | N/A
61 | AIT-4003C | Stream_3_C1 (Vol%) | Stream 3, C1 | REAL | READ | 40108 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
62 | AIT-4003D | Stream_3_C2 (Vol%) | Stream 3, C2 | REAL | READ | 40110 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
63 | AIT-4003E | Stream_3_C3 (Vol%) | Stream 3, C3 | REAL | READ | 40112 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
64 | AIT-4003F | Stream_3_iC4 (Vol%) | Stream 3, iC4 | REAL | READ | 40114 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
65 | AIT-4003G | Stream_3_nC4 (Vol%) | Stream 3, nC4 | REAL | READ | 40116 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 20/07/16
66 | AIT-4003H | Stream_3_Stream_3_Transmission | Stream 3, Transmission | REAL | READ | 40118 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal | DD/JW - 20/07/16

## IO MAP
PETRONAS - TOWN NORTH - IO MAP
DI | DESCRIPTION | STREAM | CHECKED | DO | DESCRIPTION | STREAM | CHECKED
00 | SWITCH P2 | 4050 | DD/JW - 20/07/16 | 00 | SPECTROMETER POWER | SPEC | DD/JW - 20/07/16
01 | SWITCH P3 | 4050 | DD/JW - 20/07/16 | 01 | SPARE
02 | SWITCH P2 | 4002 | DD/JW - 20/07/16 | 02 | SPARE
03 | SWITCH P3 | 4002 | DD/JW - 20/07/16 | 03 | SPARE
04 | SWITCH P2 | 4003 | DD/JW - 20/07/16 | 04 | SPARE
05 | SWITCH P3 | 4003 | DD/JW - 20/07/16 | 05 | SPARE
06 | SPARE |  |  | 07 | SPARE
07 | SPARE |  |  | 08 | VCON READY LIGHT | 4050 | DD/JW - 20/07/16
08 | SPARE |  |  | 09 | SPARE
09 | SPARE |  |  | 10 | SPARE
10 | SPARE |  |  | 11 | VCON READY LIGHT | 4002 | DD/JW - 20/07/16
11 | SPARE |  |  | 12 | SPARE
12 | SPARE |  |  | 13 | SPARE
13 | SPARE |  |  | 14 | VCON READY LIGHT | 4003 | DD/JW - 20/07/16
14 | SPARE |  |  | 15 | SPARE
15 | SPARE |  |  | 16 | SPARE
|  |  |  | 17 | SPARE
|  |  |  | 18 | SPARE
AI | DESCRIPTION | STREAM | CHECKED
P2AI00 | PRESSURE | 4050 | DD/JW - 20/07/16
P2AI01 | PRESSURE | 4002 | DD/JW - 20/07/16
P2AI02 | PRESSURE | 4003 | DD/JW - 20/07/16
P2AI03 | SPARE
P3AI00 | TEMPERATURE | 4050 | DD/JW - 20/07/16
P3AI01 | TEMPERATURE | 4002 | DD/JW - 20/07/16
P3AI02 | TEMPERATURE | 4003 | DD/JW - 20/07/16
P3AI03 | SPARE
P4AI00 | SPARE
P4AI01 | SPARE
P4AI02 | SPARE
P4AI03 | SPARE

## HMI_Datamap
| PETRONAS - TOWN NORTH - MODBUS MAP - FAT 2020/07/16 | [12 empty] | REV 1
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
1 | RESET | RESET | Reset Alarm | BOOL | WRITE | 00001 | N/A | N/A | N/A | N/A | OFF | RESET | Pulse for 2 seconds to reset latched alarms | DD/JW - 200716
2 | OBC_COMM_FAIL | OBC_COMM_FAIL | On Board Computer Communication Fault | BOOL | READ | 00002 | N/A | N/A | N/A | N/A | FAULT | OK | No change in VCON BeatModbus > 10 min | DD/JW - 200716
3 |  | SYSTEM_STSTUS | System Status | BOOL | READ | 00003 | N/A | N/A | N/A | N/A | FAULT | OK | No change in VCON BeatModbus > 10 min | DD/JW - 200716
4 | STREAM - 1 - LPG
5 | UA_4050A | Stream_1_Analyzer_Warning | Stream 1-Analyzer Common Warning Alarm | BOOL | READ | 00010 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet | DD/JW - 200716
6 | UA_4050B | Stream_1_Model_Warning | Stream 1 - Analyzer Model Quality Warning | BOOL | READ | 00011 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality | DD/JW - 200716
7 | UA_4050C | Stream_1_Sample_Panel_Warning | Stream 1-Sample Panel Common Warning Alarm | BOOL | READ | 00012 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure | DD/JW - 200716
8 | FSL_4050 | Stream_1_FSL_COND | Stream 1 - Low Sample Flow Warning | BOOL | READ | 00013 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell | NOT USED
9 | FSH_4050 | Stream_1_FSH_COND | Stream 1 - High Sample Flow Warning | BOOL | READ | 00014 | N/A | N/A | N/A | N/A | OFF | WARNING | Hi Flow Condition at Sample Cell | NOT USED
10 | PAH-4050 | Stream_1_High_Pressure_Alarm | Stream 1 - High Pressure Warning Alarm | BOOL | READ | 00015 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 200716
11 | TAH-4050 | Stream_1_High_Temperature_Alarm | Stream 1 - High Temperature Warning Alarm | BOOL | READ | 00016 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 200716
12 |  | Stream_1_Sampling_Alarm | Stream 1 - Sample Switch Warning | BOOL | READ | 00017 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min | DD/JW - 200716
13 | XA_4050A | Stream_1_Analyzer_Fault | Stream 1-Analyzer Common Fault Alarm | BOOL | READ | 00018 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet | DD/JW - 200716
14 | XA_4050B | Stream_1_Model_Fault | Stream 1 - Analyzer Model Quality Fault | BOOL | READ | 00019 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality | DD/JW - 200716
15 | XA_4050C | Stream_1_Sample_Panel_Fault | Stream 1-Sample Panel Common Fault Alarm | BOOL | READ | 00020 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure | DD/JW - 200716
16 |  | Stream_1_Temperature_Fault | Stream 1 - Temperature Transmitter Fault | BOOL | READ | 00021 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | DD/JW - 200716
17 |  | Stream_1_Pressure_Fault | Stream 1 - Pressure Transmitter Fault | BOOL | READ | 00022 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | DD/JW - 200716
18 |  | Stream_1_VCON_Normal | Stream 1 - Analyzer In Continous Analysis Mode | BOOL | READ | 00023 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
19 |  | Stream_1_VCON_Get_Ready | Stream 1 - Analyzer Sample Collection Mode Request | BOOL | READ | 00024 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
20 |  | Stream_1_VCON_Sampling | Stream 1 - Analyzer in Sample Collection Mode | BOOL | READ | 00025 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
21 |  | Stream_1_VCON_Ready | Stream 1 - Analyzer Ready For Sample Collection | BOOL | READ | 00026 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
22 |  | Stream_1_Sample_Source | Stream 1 - Sample Request Source | BOOL | READ | 00027 | N/A | N/A | N/A | N/A | HMI | SWITCH | Hardware Configuration Setting | DD/JW - 200716
23 |  | Stream_1_Active_Alarm | Stream 1 - Active Alarm | BOOL | READ | 00028 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
24 |  | Stream_1_Analyzer_Warning_Test_Enable | Stream 1 Analyzer Warning Test Enable | BOOL | READ | 00029 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
25 |  | Stream_1_Analyzer_Warning_Test | Stream 1 Analyzer Warning Test | BOOL | READ | 00030 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
26 |  | Stream_1_Analyzer_Fault_Test_Enable | Stream 1 Analyzer Fault Test Enable | BOOL | READ | 00031 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
27 |  | Stream_1_Analyzer_Fault_Test | Stream 1 Analyzer Fault Test | BOOL | READ | 00032 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
28 |  | Stream_1_Model_Warning_Test_Enable | Stream 1 Model Warning Test Enable | BOOL | READ | 00033 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
29 |  | Stream_1_Model_Warning_Test | Stream 1 Model Warning Test | BOOL | READ | 00034 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
30 |  | Stream_1_Model_Fault_Test_Enable | Stream 1 Model Fault Test Enable | BOOL | READ | 00035 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
31 |  | Stream_1_Model_Fault_Test | Stream 1 Model Fault Test | BOOL | READ | 00036 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
32 |  | Stream_1_Sample_Plan_Test_Enable | Stream 1 Sample Plan Test Enable | BOOL | READ | 00037 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
33 |  | Stream_1_Sample_Plan_Test | Stream 1 Sample Plan Test | BOOL | READ | 00038 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
34 |  | Stream_1_Transmission_Test_Enable | Stream 1 Transmission Test Enable | BOOL | READ | 00039 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
35
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
36 | STREAM - 2 - DEBUTANIZER
37 | UA_4002A | Stream_2_Analyzer_Warning | Stream 2-Analyzer Common Warning Alarm | BOOL | READ | 00050 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet | DD/JW - 200716
38 | UA_4002B | Stream_2_Model_Warning | Stream 2 - Analyzer Model Quality Warning | BOOL | READ | 00051 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality | DD/JW - 200716
39 | UA-4002C | Stream_2_Sample_Panel_Warning | Stream 2-Sample Panel Common Warning Alarm | BOOL | READ | 00052 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure | DD/JW - 200716
40 | FSL_4002 | Stream_2_FSL_COND | Stream 2 - Low Sample Flow Warning | REAL | READ | 00053 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell | NOT USED
41 | FSH-4002 | Stream_2_FSH_COND | Stream 2 - High Sample Flow Warning | REAL | READ | 00054 | N/A | N/A | N/A | N/A | OFF | WARNING | Hi Flow Condition at Sample Cell | NOT USED
42 | PAH-4002 | Stream_2_High_Pressure_Alarm | Stream 2 - High Pressure Warning Alarm | BOOL | READ | 00055 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 200716
43 | TAH-4002 | Stream_2_High_Temperature_Alarm | Stream 2 - High Temperature Warning Alarm | BOOL | READ | 00056 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 200716
44 |  | Stream_2_Sampling_Alarm | Stream 2 - Sample Switch Warning | BOOL | READ | 00057 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min | DD/JW - 200716
45 | XA-4002A | Stream_2_Analyzer_Fault | Stream 2-Analyzer Common Fault Alarm | BOOL | READ | 00058 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet | DD/JW - 200716
46 | XA-4002B | Stream_2_Model_Fault | Stream 2 - Analyzer Model Quality Fault | BOOL | READ | 00059 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality | DD/JW - 200716
47 | XA-4002C | Stream_2_Sample_Panel_Fault | Stream 2-Sample Panel Common Fault Alarm | BOOL | READ | 00060 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure | DD/JW - 200716
48 |  | SPARE | SPARE | BOOL | READ | 00061 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | DD/JW - 200716
49 |  | Stream_2_Temperature_Fault | Stream 2 - Temperature Transmitter Fault | BOOL | READ | 00062 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | DD/JW - 200716
50 |  | Stream_2_Pressure_Fault | Stream 2 - Pressure Transmitter Fault | BOOL | READ | 00063 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | DD/JW - 200716
51 |  | Stream_2_VCON_Normal | Stream 2 - Analyzer In Continous Analysis Mode | BOOL | READ | 00064 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
52 |  | Stream_2_VCON_Get_Ready | Stream 2 - Analyzer Sample Collection Mode Request | BOOL | READ | 00065 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
53 |  | Stream_2_VCON_Sampling | Stream 2 - Analyzer in Sample Collection Mode | BOOL | READ | 00066 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
54 |  | Stream_2_VCON_Ready | Stream 2 - Analyzer Ready For Sample Collection | BOOL | READ | 00067 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
55 |  | Stream_2_Sample_Source | Stream 2 - Sample Request Source | BOOL | READ | 00068 | N/A | N/A | N/A | N/A | HMI | SWITCH | Hardware Configuration Setting | DD/JW - 200716
56 |  | Stream_2_Active_Alarm | Stream 2 - Active Alarm | BOOL | READ | 00069 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
57 |  | Stream_2_Analyzer_Warning_Test_Enable | Stream 2 Analyzer Warning Test Enable | BOOL | READ | 00070 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
58 |  | Stream_2_Analyzer_Warning_Test | Stream 2 Analyzer Warning Test | BOOL | READ | 00071 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
59 |  | Stream_2_Analyzer_Fault_Test_Enable | Stream 2 Analyzer Fault Test Enable | BOOL | READ | 00072 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
60 |  | Stream_2_Analyzer_Fault_Test | Stream 2 Analyzer Fault Test | BOOL | READ | 00073 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
61 |  | Stream_2_Model_Warning_Test_Enable | Stream 2 Model Warning Test Enable | BOOL | READ | 00074 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
62 |  | Stream_2_Model_Warning_Test | Stream 2 Model Warning Test | BOOL | READ | 00075 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
63 |  | Stream_2_Model_Fault_Test_Enable | Stream 2 Model Fault Test Enable | BOOL | READ | 00076 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
64 |  | Stream_2_Model_Fault_Test | Stream 2 Model Fault Test | BOOL | READ | 00077 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
65 |  | Stream_2_Sample_Plan_Test_Enable | Stream 2 Sample Plan Test Enable | BOOL | READ | 00078 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
66 |  | Stream_2_Sample_Plan_Test | Stream 2 Sample Plan Test | BOOL | READ | 00079 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
67 |  | Stream_2_Transmission_Test_Enable | Stream 2 Transmission Test Enable | BOOL | READ | 00080 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
68
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
69 | STREAM - 3 - STABILIZER
70 | UA_4003A | Stream_3_Analyzer_Warning | Stream 3-Analyzer Common Warning Alarm | BOOL | READ | 00090 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet | DD/JW - 200716
71 | UA_4003B | Stream_3_Model_Warning | Stream 3 - Analyzer Model Quality Warning | BOOL | READ | 00091 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality | DD/JW - 200716
72 | UA-4003C | Stream_3_Sample_Panel_Warning | Stream 3-Sample Panel Common Warning Alarm | BOOL | READ | 00092 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure | DD/JW - 200716
73 | FSL_4003 | Stream_3_FSL_COND | Stream 3 - Low Sample Flow Warning | BOOL | READ | 00093 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell | NOT USED
74 | FSH-4003 | Stream_3_FSH_COND | Stream 3 - High Sample Flow Warning | BOOL | READ | 00094 | N/A | N/A | N/A | N/A | OFF | WARNING | Hi Flow Condition at Sample Cell | NOT USED
75 | PAH-4003 | Stream_3_High_Pressure_Alarm | Stream 3 - High Pressure Warning Alarm | BOOL | READ | 00095 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 200716
76 | TAH-4003 | Stream_3_High_Temperature_Alarm | Stream 3 - High Temperature Warning Alarm | BOOL | READ | 00096 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI | DD/JW - 200716
77 |  | Stream_3_Sampling_Alarm | Stream 3 - Sample Switch Warning | BOOL | READ | 00097 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min | DD/JW - 200716
78 | XA-4003A | Stream_3_Analyzer_Fault | Stream 3-Analyzer Common Fault Alarm | BOOL | READ | 00098 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet | DD/JW - 200716
79 | XA-4003B | Stream_3_Model_Fault | Stream 3 - Analyzer Model Quality Fault | BOOL | READ | 00099 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality | DD/JW - 200716
80 | XA-4003C | Stream_3_Sample_Panel_Fault | Stream 3-Sample Panel Common Fault Alarm | BOOL | READ | 00100 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure | DD/JW - 200716
81 |  | SPARE | SPARE | BOOL | READ | 00101 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | DD/JW - 200716
82 |  | Stream_3_Temperature_Fault | Stream 3 - Temperature Transmitter Fault | BOOL | READ | 00102 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | DD/JW - 200716
83 |  | Stream_3_Pressure_Fault | Stream 3 - Pressure Transmitter Fault | BOOL | READ | 00103 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault | DD/JW - 200716
84 |  | Stream_3_VCON_Normal | Stream 3 - Analyzer In Continous Analysis Mode | BOOL | READ | 00104 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
85 |  | Stream_3_VCON_Get_Ready | Stream 3 - Analyzer Sample Collection Mode Request | BOOL | READ | 00105 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
86 |  | Stream_3_VCON_Sampling | Stream 3 - Analyzer in Sample Collection Mode | BOOL | READ | 00106 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
87 |  | Stream_3_VCON_Ready | Stream 3 - Analyzer Ready For Sample Collection | BOOL | READ | 00107 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit | DD/JW - 200716
88 |  | Stream_3_Sample_Source | Stream 3 - Sample Request Source | BOOL | READ | 00108 | N/A | N/A | N/A | N/A | HMI | SWITCH | Hardware Configuration Setting | DD/JW - 200716
89 |  | Stream_3_Active_Alarm | Stream 3 - Active Alarm | BOOL | READ | 00109 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
90 |  | Stream_3_Analyzer_Warning_Test_Enable | Stream 3 Analyzer Warning Test Enable | BOOL | READ | 00110 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
91 |  | Stream_3_Analyzer_Warning_Test | Stream 3 Analyzer Warning Test | BOOL | READ | 00111 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
92 |  | Stream_3_Analyzer_Fault_Test_Enable | Stream 3 Analyzer Fault Test Enable | BOOL | READ | 00112 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
93 |  | Stream_3_Analyzer_Fault_Test | Stream 3 Analyzer Fault Test | BOOL | READ | 00113 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
94 |  | Stream_3_Model_Warning_Test_Enable | Stream 3 Model Warning Test Enable | BOOL | READ | 00114 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
95 |  | Stream_3_Model_Warning_Test | Stream 3 Model Warning Test | BOOL | READ | 00115 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
96 |  | Stream_3_Model_Fault_Test_Enable | Stream 3 Model Fault Test Enable | BOOL | READ | 00116 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
97 |  | Stream_3_Model_Fault_Test | Stream 3 Model Fault Test | BOOL | READ | 00117 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
98 |  | Stream_3_Sample_Plan_Test_Enable | Stream 3 Sample Plan Test Enable | BOOL | READ | 00118 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
99 |  | Stream_3_Sample_Plan_Test | Stream 3 Sample Plan Test | BOOL | READ | 00119 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
100 |  | Stream_3_Transmission_Test_Enable | Stream 3 Transmission Test Enable | BOOL | READ | 00120 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit | DD/JW - 200716
101
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
102 | Holding Registers
103 | PLC_YEAR | PLC_YEAR | PLC Clock Year | INT | READ | 40001 |  | 2016 | 2116 |  |  |  | Real Time Clock From PLC | DD/JW - 200716
104 | PLC_MONTH | PLC_MONTH | PLC Clock Month | INT | READ | 40002 |  | 1 | 12 |  |  |  | Real Time Clock From PLC | DD/JW - 200716
105 | PLC_DAY | PLC_DAY | PLC Clock Day | INT | READ | 40003 |  | 1 | 31 |  |  |  | Real Time Clock From PLC | DD/JW - 200716
106 | PLC_HOUR | PLC_HOUR | PLC Clock Hour | INT | READ | 40004 |  | 0 | 24 |  |  |  | Real Time Clock From PLC | DD/JW - 200716
107 | PLC_MINUTE | PLC_MINUTE | PLC Clock Minute | INT | READ | 40005 |  | 0 | 60 |  |  |  | Real Time Clock From PLC | DD/JW - 200716
108 | PLC_SECOND | PLC_SECOND | PLC Clock Second | INT | READ | 40006 |  | 0 | 60 |  |  |  | Real Time Clock From PLC | DD/JW - 200716
109 | CT-4000 | CT_4000 | Communications Heartbeat Register to DCS | INT | READ | 40007 | N/A | 0 | 60 | N/A | N/A | N/A | PLC Clock Seconds passed onto master controller. Alarm if value has not changed after set time. | DD/JW - 200716
110 |  | STREAMS_ENABLED | Number of Streams Enabled in Logic | INT | READ | 40008 | N/A | 0 | 4 | N/A | N/A | N/A | Configuration Parameter | DD/JW - 200716
111
112 | STREAM - 1 - LPG
113 | PIT-4104 | Stream_1_Pressure | Stream 1, Pressure | REAL | READ | 40010 | N/A | 0 | 5000 | kPag | N/A | N/A |  | DD/JW - 200716
114 | TIT-4050 | Stream_1_Temperature | Stream 1, Temperature | REAL | READ | 40012 | N/A | -20 | 80 | C | N/A | N/A |  | DD/JW - 200716
115 | AIT-4050A | Stream_1_C1 (Mol%) | Stream 1, C1 | REAL | READ | 40014 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 200716
116 | AIT-4050B | Stream_1_C2 (Mol%) | Stream 1, C2 | REAL | READ | 40016 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 200716
117 | AIT-4050C | Stream_1_C3 (Mol%) | Stream 1, C3 | REAL | READ | 40018 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 200716
118 | AIT-4050D | Stream_1_iC4 (Mol%) | Stream 1, iC4 | REAL | READ | 40020 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 200716
119 | AIT-4050E | Stream_1_nC4 (Mol%) | Stream 1, nC4 | REAL | READ | 40022 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 200716
120 | AIT-4050F | Stream_1_iC5 (Mol%) | Stream 1, iC5 | REAL | READ | 40024 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 200716
121 | AIT-4050G | Stream_1_nC5 (Mol%) | Stream 1, nC5 | REAL | READ | 40026 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 200716
122 | AIT-4050H | Stream_1_C6+ (Mol%) | Stream 1, C6 plus | REAL | READ | 40028 | N/A | 0 | 100 | MOL% | N/A | N/A |  | DD/JW - 200716
123 | AIT-4050J | Stream_1_Transmission | Stream 1, Transmission | REAL | READ | 40030 | N/A | 0 | 100 | % | N/A | N/A |  | DD/JW - 200716
124 |  | Stream_1_Sample_Mode | Stream 1, Sampling Mode | INT | READ | 40032 | N/A | 0 | 4 | N/A | N/A | N/A |  | DD/JW - 200716
125 |  | Stream_1_Sample_Mode_HMI_Select | Stream 1, Sampling Mode HMI Select | INT | READ | 40033 | N/A | 0 | 1 | N/A | N/A | N/A |  | DD/JW - 200716
126 |  | Stream_1_Pressure_Range_Lo | Stream 1, Cell Pressure Scale Low SP | REAL | READ | 40034 | N/A | 0 | 100 | kPag | N/A | N/A |  | DD/JW - 200716
127 |  | Stream_1_Pressure_Range_Hi | Stream 1, Cell Pressure Scale High SP | REAL | READ | 40036 | N/A | 0 | 100 | kPag | N/A | N/A |  | DD/JW - 200716
128 |  | Stream_1_Pressure_Alarm_Hi_SP | Stream 1, Cell Pressure Scale High Alarm SP | REAL | READ | 40038 | N/A | 0 | 100 | kPag | N/A | N/A |  | DD/JW - 200716
129 |  | Stream_1_Temperature_Range_Lo | Stream 1, Cell Temperature Scale Low SP | REAL | READ | 40040 | N/A | 0 | 300 | C | N/A | N/A |  | DD/JW - 200716
130 |  | Stream_1_Temperature_Range_Hi | Stream 1, Cell Temperature Scale High SP | REAL | READ | 40042 | N/A | 0 | 300 | C | N/A | N/A |  | DD/JW - 200716
131 |  | Stream_1_Temperature_Alarm_Hi_SP | Stream 1, Cell Temperature Scale High Alarm SP | REAL | READ | 40044 | N/A | 0 | 300 | C | N/A | N/A | Analyzer Diagnostic Signal | DD/JW - 200716
132 |  | Stream_1_Transmission_Test | Stream 1 Transmission Test | REAL | R/W | 40046 | N/A | 0 | 300 | % | N/A | N/A |  | DD/JW - 200716
133
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
134 | STREAM - 2 - DEBUTANIZER
135 | PIT-4002 | Stream_2_Pressure_1 | Stream 2, Pressure | REAL | READ | 40060 | N/A | 0 | 2000 | kPag | N/A | N/A |  | DD/JW - 200716
136 | TIT-4002 | Stream_2_Temperature_1 | Stream 2, Temperature | REAL | READ | 40062 | N/A | -20 | 80 | C | N/A | N/A |  | DD/JW - 200716
137 | AIT-4002A | Stream_2_Deemed C4 | Stream 2, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40064 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
138 | AIT-4002B | Stream_2_VPCR | Stream 2, VAPOUR PRESSURE D6377 | REAL | READ | 40066 | N/A | 0 | 100 | kPaa | N/A | N/A | NOT USED ON THIS APP | N/A
139 | AIT-4002C | Stream_2_C1 (Vol%) | Stream 2, C1 | REAL | READ | 40068 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
140 | AIT-4002D | Stream_2_C2 (Vol%) | Stream 2, C2 | REAL | READ | 40070 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
141 | AIT-4002E | Stream_2_C3 (Vol%) | Stream 2, C3 | REAL | READ | 40072 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
142 | AIT-4002F | Stream_2_iC4 (Vol%) | Stream 2, iC4 | REAL | READ | 40074 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
143 | AIT-4002G | Stream_2_nC4 (Vol%) | Stream 2, nC4 | REAL | READ | 40076 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
144 | AIT-4002H | Stream_2_Stream_2_Transmission | Stream 2, Transmission | REAL | READ | 40078 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal | DD/JW - 200716
145 |  | Stream_2_Sample_Mode | Stream 2, Sampling Mode | INT | READ | 40080 | N/A | 0 | 3 | N/A | N/A | N/A | 0=Normal, 1=Get Ready, 2=Ready, 3=Sampling | DD/JW - 200716
146 |  | Stream_2_Sample_Mode_HMI_Select | Stream 2, Sampling Mode HMI Select | INT | R/W | 40081 | N/A | 0 | 2 | N/A | N/A | N/A | 1 = HMI P2, 2 = HMI P3 | DD/JW - 200716
147 |  | Stream_2_Pressure_Range_Lo | Stream 2, Cell Pressure Scale Low SP | REAL | R/W | 40082 | N/A | 0 | 10000 | kpa | N/A | N/A |  | DD/JW - 200716
148 |  | Stream_2_Pressure_Range_Hi | Stream 2, Cell Pressure Scale High SP | REAL | R/W | 40084 | N/A | 0 | 10000 | kpa | N/A | N/A |  | DD/JW - 200716
149 |  | Stream_2_Pressure_Alarm_Hi_SP | Stream 2, Cell Pressure Scale High Alarm SP | REAL | R/W | 40086 | N/A | 0 | 10000 | kpa | N/A | N/A |  | DD/JW - 200716
150 |  | Stream_2_Temperature_Range_Lo | Stream 2, Cell Temperature Scale Low SP | REAL | R/W | 40088 | N/A | 0 | 300 | C | N/A | N/A |  | DD/JW - 200716
151 |  | Stream_2_Temperature_Range_Hi | Stream 2, Cell Temperature Scale High SP | REAL | R/W | 40090 | N/A | 0 | 300 | C | N/A | N/A |  | DD/JW - 200716
152 |  | Stream_2_Temperature_Alarm_Hi_SP | Stream 2, Cell Temperature Scale High Alarm SP | REAL | R/W | 40092 | N/A | 0 | 300 | C | N/A | N/A |  | DD/JW - 200716
153 |  | Stream_2_Transmission_Test | Stream 2 Transmission Test | REAL | R/W | 40094 | N/A | 0 | 100 | % | N/A | N/A |  | DD/JW - 200716
154 | [13 empty] | DD/JW - 200716
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
155 | STREAM - 3 - STABILIZER
156 | PIT-4003 | Stream_3_Pressure_1 | Stream 3, Pressure | REAL | READ | 40100 | N/A | 0 | 2000 | kPag | N/A | N/A |  | DD/JW - 200716
157 | TIT-4003 | Stream_3_Temperature_1 | Stream 3, Temperature | REAL | READ | 40102 | N/A | -20 | 80 | C | N/A | N/A |  | DD/JW - 200716
158 | AIT-4003A | Stream_3_Deemed C4 | Stream 3, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40104 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
159 | AIT-4003B | Stream_3_VPCR | Stream 3, VAPOUR PRESSURE D6377 | REAL | READ | 40106 | N/A | 0 | 100 | kPa | N/A | N/A | NOT USED ON THIS APP | N/A
160 | AIT-4003C | Stream_3_C1 (Vol%) | Stream 3, C1 | REAL | READ | 40108 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
161 | AIT-4003D | Stream_3_C2 (Vol%) | Stream 3, C2 | REAL | READ | 40110 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
162 | AIT-4003E | Stream_3_C3 (Vol%) | Stream 3, C3 | REAL | READ | 40112 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
163 | AIT-4003F | Stream_3_iC4 (Vol%) | Stream 3, iC4 | REAL | READ | 40114 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
164 | AIT-4003G | Stream_3_nC4 (Vol%) | Stream 3, nC4 | REAL | READ | 40116 | N/A | 0 | 100 | VOL% | N/A | N/A |  | DD/JW - 200716
165 | AIT-4003H | Stream_3_Stream_3_Transmission | Stream 3, Transmission | REAL | READ | 40118 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal | DD/JW - 200716
166 |  | Stream_3_Sample_Mode | Stream 3, Sampling Mode | INT | READ | 40120 | N/A | 0 | 3 | N/A | N/A | N/A | 0=Normal, 1=Get Ready, 2=Ready, 3=Sampling | DD/JW - 200716
167 |  | Stream_3_Sample_Mode_HMI_Select | Stream 3, Sampling Mode HMI Select | INT | R/W | 40121 | N/A | 0 | 2 | N/A | N/A | N/A | 1 = HMI P2, 2 = HMI P3 | DD/JW - 200716
168 |  | Stream_3_Pressure_Range_Lo | Stream 3, Cell Pressure Scale Low SP | REAL | R/W | 40122 | N/A | 0 | 10000 | kpa | N/A | N/A |  | DD/JW - 200716
169 |  | Stream_3_Pressure_Range_Hi | Stream 3, Cell Pressure Scale High SP | REAL | R/W | 40124 | N/A | 0 | 10000 | kpa | N/A | N/A |  | DD/JW - 200716
170 |  | Stream_3_Pressure_Alarm_Hi_SP | Stream 3, Cell Pressure Scale High Alarm SP | REAL | R/W | 40126 | N/A | 0 | 10000 | kpa | N/A | N/A |  | DD/JW - 200716
171 |  | Stream_3_Temperature_Range_Lo | Stream 3, Cell Temperature Scale Low SP | REAL | R/W | 40128 | N/A | 0 | 300 | C | N/A | N/A |  | DD/JW - 200716
172 |  | Stream_3_Temperature_Range_Hi | Stream 3, Cell Temperature Scale High SP | REAL | R/W | 40130 | N/A | 0 | 300 | C | N/A | N/A |  | DD/JW - 200716
173 |  | Stream_3_Temperature_Alarm_Hi_SP | Stream 3, Cell Temperature Scale High Alarm SP | REAL | R/W | 40132 | N/A | 0 | 300 | C | N/A | N/A |  | DD/JW - 200716
174 |  | Stream_3_Transmission_Test | Stream 3 Transmission Test | REAL | R/W | 40134 | N/A | 0 | 100 | % | N/A | N/A |  | DD/JW - 200716
175

## LPG 4050 (CH1)
LPG (CH1)
SPECIES | REG TYPE | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1_MOL | Input | 7001 | 8001 | 32-bit Floating Point | MOL%
C2_MOL | Input | 7003 | 8003 | 32-bit Floating Point | MOL%
C3_MOL | Input | 7005 | 8005 | 32-bit Floating Point | MOL%
iC4_MOL | Input | 7007 | 8007 | 32-bit Floating Point | MOL%
nC4_MOL | Input | 7009 | 8009 | 32-bit Floating Point | MOL%
iC5_MOL | Input | 7011 | 8011 | 32-bit Floating Point | MOL%
nC5_MOL | Input | 7013 | 8013 | 32-bit Floating Point | MOL%
C6_MOL | Input | 7015 | 8015 | 32-bit Floating Point | MOL%
Temperature_1 | Input | 7017 | 8017 | 32-bit Floating Point | MOL%
Pressure_1 | Input | 7019 | 8019 | 32-bit Floating Point | MOL%
Transmission_1 | Input | 7021 | 8021 | 32-bit Floating Point | MOL%
Fault_Ireg | Input | 7023 | 8023 | 16-bit Integer | ENCODED
Warning_Ireg | Input | 7024 | 8024 | 16-bit Integer | ENCODED
Alarm IReg | Input | 7025 | 8025 | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
Model IReg | Input | 7026 | 8026 | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7027 | 8027 | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7028 | 8028 | 16-bit Integer | 41=Trigger to pull sample
INPUTS
Temperature_1 | Holding | 1 | N/A | 16-bit Integer
Pressure_1 | Holding | 2 | N/A | 16-bit Integer
vcon trigger | Holding | 3 | N/A | 16-bit Integer
no flow | Holding | 4 | N/A | 16-bit Integer
vcon_get_ready | Holding | 21 | N/A | 16-bit Integer | 41=VCON GET READY
vcon_sample | Holding | 22 | N/A | 16-bit Integer | 41=SAMPLE IN PROGRESS
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer | REMOTE POWER CYCLE
Status_Modbus | Input | 7097 | N/A | 16-bit Integer | STREAM INDICATOR
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer | TOGGLE BETWENN 0 AND 41
prefix: PT_

## DEBUTANIZER (CH2)
DEBUTANIZER
SPECIES | REG TYPE | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1_VOL | Input | 7101 | 8101 | 32-bit Floating Point | VOL%
C2_VOL | Input | 7103 | 8103 | 32-bit Floating Point | VOL%
C3_VOL | Input | 7105 | 8105 | 32-bit Floating Point | VOL%
iC4_VOL | Input | 7107 | 8107 | 32-bit Floating Point | VOL%
nC4_VOL | Input | 7109 | 8109 | 32-bit Floating Point | VOL%
DEEMED_C4 | Input | 7111 | 8111 | 32-bit Floating Point | VOL%
SPARE | Input | 7113 | 8113 | 32-bit Floating Point | kPaa
SPARE | Input | 7115 | 8115 | 32-bit Floating Point
Temperature_1 | Input | 7117 | 8117 | 32-bit Floating Point | MOL%
Pressure_1 | Input | 7119 | 8119 | 32-bit Floating Point | MOL%
Transmission_1 | Input | 7121 | 8121 | 32-bit Floating Point | MOL%
Fault_Ireg | Input | 7123 | 8123 | 16-bit Integer | ENCODED
Warning_Ireg | Input | 7124 | 8124 | 16-bit Integer | ENCODED
Alarm IReg | Input | 7125 | 8125 | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
Model IReg | Input | 7126 | 8126 | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7127 | 8127 | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7128 | 8128 | 16-bit Integer | 41=Trigger to pull sample
INPUTS
Temperature_1 | Holding | 5 | N/A | 16-bit Integer
Pressure_1 | Holding | 6 | N/A | 16-bit Integer
vcon trigger | Holding | 7 | N/A | 16-bit Integer
no flow | Holding | 8 | N/A | 16-bit Integer
vcon_get_ready | Holding | 23 | N/A | 16-bit Integer | 41=VCON GET READY
vcon_sample | Holding | 24 | N/A | 16-bit Integer | 41=SAMPLE IN PROGRESS
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer | REMOTE POWER CYCLE
Status_Modbus | Input | 7097 | N/A | 16-bit Integer | STREAM INDICATOR
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer | TOGGLE BETWENN 0 AND 41

## STABILIZER (CH3)
DEBUTANIZER
SPECIES | REG TYPE | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1_VOL | Input | 7201 | 8201 | 32-bit Floating Point | VOL%
C2_VOL | Input | 7203 | 8203 | 32-bit Floating Point | VOL%
C3_VOL | Input | 7205 | 8205 | 32-bit Floating Point | VOL%
iC4_VOL | Input | 7207 | 8207 | 32-bit Floating Point | VOL%
nC4_VOL | Input | 7209 | 8209 | 32-bit Floating Point | VOL%
DEEMED_C4 | Input | 7211 | 8211 | 32-bit Floating Point | VOL%
SPARE | Input | 7213 | 8213 | 32-bit Floating Point | kPaa
SPARE | Input | 7215 | 8215 | 32-bit Floating Point
Temperature_1 | Input | 7217 | 8217 | 32-bit Floating Point | MOL%
Pressure_1 | Input | 7219 | 8219 | 32-bit Floating Point | MOL%
Transmission_1 | Input | 7221 | 8221 | 32-bit Floating Point | MOL%
Fault_Ireg | Input | 7223 | 8223 | 16-bit Integer | ENCODED
Warning_Ireg | Input | 7224 | 8224 | 16-bit Integer | ENCODED
Alarm IReg | Input | 7225 | 8225 | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
Model IReg | Input | 7226 | 8226 | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7227 | 8227 | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7228 | 8228 | 16-bit Integer | 41=Trigger to pull sample
INPUTS
Temperature_1 | Holding | 9 | N/A | 16-bit Integer
Pressure_1 | Holding | 10 | N/A | 16-bit Integer
vcon trigger | Holding | 11 | N/A | 16-bit Integer
no flow | Holding | 12 | N/A | 16-bit Integer
vcon_get_ready | Holding | 25 | N/A | 16-bit Integer | 41=VCON GET READY
vcon_sample | Holding | 26 | N/A | 16-bit Integer | 41=SAMPLE IN PROGRESS
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer | REMOTE POWER CYCLE
Status_Modbus | Input | 7097 | N/A | 16-bit Integer | STREAM INDICATOR
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer | TOGGLE BETWENN 0 AND 41

## CHANGE LOG
DATE | CHANGES | BY
2020-07-17 | FAT COMPLETE - AS BUILT VERSION | DD

## DataTypes (hidden)
Data Type | Description
BOOL | Boolean, Single bit
WORD | Unsigned 16 bit value bit 0 is the low bit bit 15 is the high bit
SHORT | Signed 16 bit value bit 0 is the low bit bit 14 is the high bit bit 15 is the sign bit
DWORD | Unsigned 32 bit value bit 0 is the low bit bit 31 is the high bit
LONG | Signed 32 bit value bit 0 is the low bit bit 30 is the high bit bit 31 is the sign bit
BCD | Two byte packed BCD Value range is 0-9999. Behavior is undefined for values beyond this range.
LBCD | Four byte packed BCD Value range is 0-99999999. Behavior is undefined for values beyond this range.
STRING | Null terminated ASCII string Supported on Modbus Model, includes Hi-Lo Lo-Hi byte order selection.
DOUBLE (Note 1) | 64 bit floating point value The driver interprets four consecutive registers as a double precision value by making the last two registers the high DWord and the first two registers the low DWord.
DOUBLE Example | If register 40001 is specified as a double, bit 0 of register 40001 would be bit 0 of the 64 bit data type and bit 15 of register 40004 would be bit 63 of the 64 bit data type.
FLOAT (Note 1) | 32 bit floating point value The driver interprets two consecutive registers as a single precision value by making the last register the high word and the first register the low word.
FLOAT Example | If register 40001 is specified as a float, bit 0 of register 40001 would be bit 0 of the 32 bit data type and bit 15 of register 40002 would be bit 31 of the 32 bit data type.
Notes:
1. The descriptions assume the default; that is, first DWord low data handling of 64 bit data types and first word
low data handling of 32 bit data types.
2. Standard data format names have been selected. If other names are desired, specify the bytes and range.