## DATASHEET
AUTOMATION DATA SHEET
PROJECT/CLIENT |  | 7 Generations
SITE LOCATION |  | 07-11-064-04 W6M KARR Gas Plant Grande Prairie
HARWARE CONFIGURATION
ANALYZER |  |  | CTX |  |  | 40-AIT-124
PLC |  |  | MICRO850
HMI |  |  | 5" PROFACE
STREAM 1 |  | TAG | 40-AIT-400 |  | PROCESS |  | Condy
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  | kPag | 0
[5 empty] | HIGH RANGE |  | 2000 |  | kPag | 7000 | psig | 400 | 60
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | -20 |  | C |  |  | 1850 | 264.2857
[5 empty] | HIGH RANGE |  | 100 |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | SWITCH |  | INTERRUPTION VALVE |  | PNUEMATIC
STREAM 2 |  | TAG | 50-AIT-400 |  | PROCESS |  | Condy
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  |  | 0
[5 empty] | HIGH RANGE |  | 2000 |  | kPag | 7000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | -20 |  | C
[5 empty] | HIGH RANGE |  | 100 |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | SWITCH |  | INTERRUPTION VALVE |  | PNUEMATIC
STREAM 3 |  | TAG | 60-AIT-400 |  | PROCESS |  | Condy
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  |  | 0
[5 empty] | HIGH RANGE |  | 2000 |  | kPag | 7000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | -20
[5 empty] | HIGH RANGE |  | 100 |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | N/A |  | INTERRUPTION VALVE |  | PNUEMATIC
STREAM 4 |  | TAG | N/A |  | PROCESS |  | N/A
PRESSURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE |  | 0 |  |  | 0
[5 empty] | HIGH RANGE |  |  |  | kPag | 1000 | psig
TEMPERATURE MEASUREMENT |  |  | TRANSMITTER |  | LOW RANGE
[5 empty] | HIGH RANGE |  |  |  | C
FLOW MEASUREMENT |  |  | SWITCH |  | LOW RANGE |  | N/A
[5 empty] | HIGH RANGE |  | N/A
SAMPLING AUTOMATION |  |  | N/A |  | INTERRUPTION VALVE |  | N/A
SOFTWARE CONFIGURATION
COMMUNICATION |  |  | TCP/IP MODBUS
OUTPUTS |  |  | 3 | QTY | Interrupt Valve
|  |  | 3 | QTY | Deemed C4
COMPONENTS
| STREAM 1 | TAG | 40-AIT-400 |  |  | STREAM 2 | TAG | 50-AIT-400
| PROCESS | Condy |  |  |  | PROCESS | Condy
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | VOL% |  |  |  |  | VOL%
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
| STREAM 3 | TAG | 60-AIT-400 |  |  | STREAM 4 | TAG | N/A
| PROCESS | Condy |  |  |  | PROCESS | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | VOL% |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
|  |  |  | N/A |  |  |  |  | N/A
LOOKUP TABLES FOR DROP DOWNS
TRANSMITTER | CTX | MOL% | RTD |  | SWITCH |  | SWITCH
SENSOR | SSL | VOL% | TRANSMITTER |  | TRANSMITTER |  | AUTO
N/A | N/A | N/A | N/A |  | N/A |  | N/A
ELECTRIC |  | MICRO850 |  | 5" PROFACE |  |  | TCP/IP MODBUS
PNUEMATIC |  | MICRO820 |  | 7" PANELVIEW 800 |  |  | RS-485 MODBUS
N/A |  | N/A |  | 10" REDLION |  |  | RS-232 MODBUS
N/A
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
C2/C3 RATIO
C1/C3 RATIO
DEEMED C4
VPCR4
C1
C2
C3
iC4
nC4
iC5
nC5
C6+
C7
C8
C9
C10
C11
C12
DO
AO

## IO MAP
7GENS - KARR GASS PLANT - IO MAP
DI | DESCRIPTION | STREAM | CHECKED | DO | DESCRIPTION | TAG | CHECKED
00 | SWITCH P2 | 40-AIT-400 |  | 00 | SPECTROMETER POWER | SPEC
01 | SWITCH P3 | 40-AIT-400 |  | 01 | SPARE
02 | SWITCH P2 | 50-AIT-400 |  | 02 | SPARE
03 | SWITCH P3 | 50-AIT-400 |  | 03 | SPARE
04 | SWITCH P2 | 60-AIT-400 |  | 04 | SPARE
05 | SWITCH P3 | 60-AIT-400 |  | 05 | SPARE
06 | SPARE |  |  | 07 | SPARE
07 | SPARE |  |  | 08 | VCON READY LIGHT | 40-UAL-400
08 | FSL | 40-FLS-400 |  | 09 | INTERRUPT SOLENOID | 40-EY-400
09 | SPARE |  |  | 10 | SPARE
10 | FLS | 50-FSL-400 |  | 11 | VCON READY LIGHT | 50-UAL-400
11 | SPARE |  |  | 12 | INTERRUPT SOLENOID | 50-EY-400
12 | FLS | 60-FLS-400 |  | 13 | SPARE
13 | SPARE |  |  | 14 | VCON READY LIGHT | 60-UAL-400
14 | SPARE |  |  | 15 | INTERRUPT SOLENOID | 60-EY-400
15 | SPARE |  |  | 16 | SPARE
|  |  |  | 17 | SPARE
|  |  |  | 18 | SPARE
AI | DESCRIPTION | TAG | CHECKED | AO | DESCRIPTION | STREAM | CHECKED
P2AI00 | PRESSURE | 40-PIT-400 |  | P4AO-00 | DEEMED C4 | 40-AIT-400
P2AI01 | PRESSURE | 50-PIT-400 |  | P4A0-01 | DEEMED C4 | 50-AIT-400
P2AI02 | SPARE |  |  | P5AO-00 | DEEMED C4 | 60-AIT-400
P2AI03 | PRESSURE | 60-PIT-400 |  | P5AO-01 | SPARE
P3AI00 | TEMPERATURE | 40-TIT-400
P3AI01 | SPARE
P3AI02 | TEMPERATURE | 60-TIT-400
P2AI03 | SPARE

## MASTER MODBUS MAP
| 7 GENERATIONS - KARR GAS PLANT - CLIENT MODBUS MAP - INITIAL DRAFT 20082020 | [12 empty] | REV 1
| Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
1 | RESET | RESET | Reset Alarm | BOOL | WRITE | 00001 | N/A | N/A | N/A | N/A | OFF | RESET | Pulse for 2 seconds to reset latched alarms
2 | OBC_COMM_FAIL | OBC_COMM_FAIL | On Board Computer Communication Fault | BOOL | READ | 00002 | N/A | N/A | N/A | N/A | FAULT | OK | No change in VCON BeatModbus > 10 min
4 | STREAM - 1 - CONDENSATE
5 | 40-UA_400A | Stream_1_Analyzer_Warning | Stream 1-Analyzer Common Warning Alarm | BOOL | READ | 00010 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
6.5 | 40-UA_400B | Stream_1_Model_Warning | Stream 1 - Analyzer Model Quality Warning | BOOL | READ | 00011 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
7.9 | 40-UA_400C | Stream_1_Sample_Panel_Warning | Stream 1-Sample Panel Common Warning Alarm | BOOL | READ | 00012 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
9.3 | 40-FSL_400 | Stream_1_FSL_COND | Stream 1 - Low Sample Flow Warning | BOOL | READ | 00013 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
10.7 | 40-PAH-400 | Stream_1_High_Pressure_Alarm | Stream 1 - High Pressure Warning Alarm | BOOL | READ | 00015 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
12.1 | 40-TAH-400 | Stream_1_High_Temperature_Alarm | Stream 1 - High Temperature Warning Alarm | BOOL | READ | 00016 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
13.5 |  | Stream_1_Sampling_Alarm | Stream 1 - Sample Switch Warning | BOOL | READ | 00017 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
14.9 | 40-XA_400A | Stream_1_Analyzer_Fault | Stream 1-Analyzer Common Fault Alarm | BOOL | READ | 00018 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
16.3 | 40-XA_400B | Stream_1_Model_Fault | Stream 1 - Analyzer Model Quality Fault | BOOL | READ | 00019 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
17.7 | 40-XA_400C | Stream_1_Sample_Panel_Fault | Stream 1-Sample Panel Common Fault Alarm | BOOL | READ | 00020 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
19.1 |  | Stream_1_Temperature_Fault | Stream 1 - Temperature Transmitter Fault | BOOL | READ | 00021 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
20.5 |  | Stream_1_Pressure_Fault | Stream 1 - Pressure Transmitter Fault | BOOL | READ | 00022 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
21.9 |  | Stream_1_VCON_Normal | Stream 1 - Analyzer In Continous Analysis Mode | BOOL | READ | 00023 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
23.3 |  | Stream_1_VCON_Get_Ready | Stream 1 - Analyzer Sample Collection Mode Request | BOOL | READ | 00024 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
24.7 |  | Stream_1_VCON_Sampling | Stream 1 - Analyzer in Sample Collection Mode | BOOL | READ | 00025 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
26.1 |  | Stream_1_VCON_Ready | Stream 1 - Analyzer Ready For Sample Collection | BOOL | READ | 00026 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
27.5 |  | Stream_1_Sample_Source | Stream 1 - Sample Request Source | BOOL | READ | 00027 | N/A | N/A | N/A | N/A | HMI | SWITCH | Hardware Configuration Setting
28.9 |  | Stream_1_Active_Alarm | Stream 1 - Active Alarm | BOOL | READ | 00028 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
30.3 |  | Stream_1_Analyzer_Warning_Test_Enable | Stream 1 Analyzer Warning Test Enable | BOOL | READ | 00029 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
31.7 |  | Stream_1_Analyzer_Warning_Test | Stream 1 Analyzer Warning Test | BOOL | READ | 00030 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
33.1 |  | Stream_1_Analyzer_Fault_Test_Enable | Stream 1 Analyzer Fault Test Enable | BOOL | READ | 00031 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
34.5 |  | Stream_1_Analyzer_Fault_Test | Stream 1 Analyzer Fault Test | BOOL | READ | 00032 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
35.9 |  | Stream_1_Model_Warning_Test_Enable | Stream 1 Model Warning Test Enable | BOOL | READ | 00033 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
37.3 |  | Stream_1_Model_Warning_Test | Stream 1 Model Warning Test | BOOL | READ | 00034 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
38.7 |  | Stream_1_Model_Fault_Test_Enable | Stream 1 Model Fault Test Enable | BOOL | READ | 00035 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
40.1 |  | Stream_1_Model_Fault_Test | Stream 1 Model Fault Test | BOOL | READ | 00036 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
41.5 |  | Stream_1_Sample_Plan_Test_Enable | Stream 1 Sample Plan Test Enable | BOOL | READ | 00037 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
42.9 |  | Stream_1_Sample_Plan_Test | Stream 1 Sample Plan Test | BOOL | READ | 00038 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
44.3 |  | Stream_1_Transmission_Test_Enable | Stream 1 Transmission Test Enable | BOOL | READ | 00039 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
45.7
47.1 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
48.5 | STREAM - 2 - CONDENSATE
49.9 | 50-UA_400A | Stream_2_Analyzer_Warning | Stream 2-Analyzer Common Warning Alarm | BOOL | READ | 00050 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
51.3 | 50-UA_400B | Stream_2_Model_Warning | Stream 2 - Analyzer Model Quality Warning | BOOL | READ | 00051 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
52.7 | 50-UA_400C | Stream_2_Sample_Panel_Warning | Stream 2-Sample Panel Common Warning Alarm | BOOL | READ | 00052 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
54.1 | 50-FSL_400 | Stream_2_FSL_COND | Stream 2 - Low Sample Flow Warning | REAL | READ | 00053 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
55.5 | 50-PAH-400 | Stream_2_High_Pressure_Alarm | Stream 2 - High Pressure Warning Alarm | BOOL | READ | 00055 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
56.9 | 50-TAH-400 | Stream_2_High_Temperature_Alarm | Stream 2 - High Temperature Warning Alarm | BOOL | READ | 00056 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
58.3 |  | Stream_2_Sampling_Alarm | 400 | BOOL | READ | 00057 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
59.7 | 50-XA_400A | Stream_2_Analyzer_Fault | Stream 2-Analyzer Common Fault Alarm | BOOL | READ | 00058 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
61.1 | 50-XA_400B | Stream_2_Model_Fault | Stream 2 - Analyzer Model Quality Fault | BOOL | READ | 00059 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
62.5 | 50-XA_400C | Stream_2_Sample_Panel_Fault | Stream 2-Sample Panel Common Fault Alarm | BOOL | READ | 00060 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
63.9 |  | SPARE | SPARE | BOOL | READ | 00061 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
65.3 |  | Stream_2_Temperature_Fault | Stream 2 - Temperature Transmitter Fault | BOOL | READ | 00062 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
66.7 |  | Stream_2_Pressure_Fault | Stream 2 - Pressure Transmitter Fault | BOOL | READ | 00063 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
68.1 |  | Stream_2_VCON_Normal | Stream 2 - Analyzer In Continous Analysis Mode | BOOL | READ | 00064 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
69.5 |  | Stream_2_VCON_Get_Ready | Stream 2 - Analyzer Sample Collection Mode Request | BOOL | READ | 00065 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
70.9 |  | Stream_2_VCON_Sampling | Stream 2 - Analyzer in Sample Collection Mode | BOOL | READ | 00066 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
72.3 |  | Stream_2_VCON_Ready | Stream 2 - Analyzer Ready For Sample Collection | BOOL | READ | 00067 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
73.7 |  | Stream_2_Sample_Source | Stream 2 - Sample Request Source | BOOL | READ | 00068 | N/A | N/A | N/A | N/A | HMI | SWITCH | Hardware Configuration Setting
75.1 |  | Stream_2_Active_Alarm | Stream 2 - Active Alarm | BOOL | READ | 00069 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
76.5 |  | Stream_2_Analyzer_Warning_Test_Enable | Stream 2 Analyzer Warning Test Enable | BOOL | READ | 00070 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
77.9 |  | Stream_2_Analyzer_Warning_Test | Stream 2 Analyzer Warning Test | BOOL | READ | 00071 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
79.3 |  | Stream_2_Analyzer_Fault_Test_Enable | Stream 2 Analyzer Fault Test Enable | BOOL | READ | 00072 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
80.7 |  | Stream_2_Analyzer_Fault_Test | Stream 2 Analyzer Fault Test | BOOL | READ | 00073 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
82.1 |  | Stream_2_Model_Warning_Test_Enable | Stream 2 Model Warning Test Enable | BOOL | READ | 00074 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
83.5 |  | Stream_2_Model_Warning_Test | Stream 2 Model Warning Test | BOOL | READ | 00075 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
84.9 |  | Stream_2_Model_Fault_Test_Enable | Stream 2 Model Fault Test Enable | BOOL | READ | 00076 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
86.3 |  | Stream_2_Model_Fault_Test | Stream 2 Model Fault Test | BOOL | READ | 00077 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
87.7 |  | Stream_2_Sample_Plan_Test_Enable | Stream 2 Sample Plan Test Enable | BOOL | READ | 00078 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
89.1 |  | Stream_2_Sample_Plan_Test | Stream 2 Sample Plan Test | BOOL | READ | 00079 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
90.5 |  | Stream_2_Transmission_Test_Enable | Stream 2 Transmission Test Enable | BOOL | READ | 00080 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
91.9
93.3 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
94.7 | STREAM - 3 - CONDENSATE
96.1 | 60-UA_400A | Stream_3_Analyzer_Warning | Stream 3-Analyzer Common Warning Alarm | BOOL | READ | 00090 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Analyzer Control Cabinet
97.5 | 60-UA_400B | Stream_3_Model_Warning | Stream 3 - Analyzer Model Quality Warning | BOOL | READ | 00091 | N/A | N/A | N/A | N/A | OFF | WARNING | Calibration Quality
98.9 | 60-UA_400C | Stream_3_Sample_Panel_Warning | Stream 3-Sample Panel Common Warning Alarm | BOOL | READ | 00092 | N/A | N/A | N/A | N/A | OFF | WARNING | Warning Local To Sample System Enclosure
100.3 | 60-FSL_400 | Stream_3_FSL_COND | Stream 3 - Low Sample Flow Warning | BOOL | READ | 00093 | N/A | N/A | N/A | N/A | OFF | WARNING | No Flow Condition at Sample Cell
101.7 | 60-PAH-400 | Stream_3_High_Pressure_Alarm | Stream 3 - High Pressure Warning Alarm | BOOL | READ | 00095 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
103.1 | 60-TAH-400 | Stream_3_High_Temperature_Alarm | Stream 3 - High Temperature Warning Alarm | BOOL | READ | 00096 | N/A | N/A | N/A | N/A | OFF | WARNING | Setpoint Local to HMI
104.5 |  | Stream_3_Sampling_Alarm | Stream 3 - Sample Switch Warning | BOOL | READ | 00097 | N/A | N/A | N/A | N/A | OFF | WARNING | Left in SAMPLE mode > 20 min
105.9 | 60-XA_400A | Stream_3_Analyzer_Fault | Stream 3-Analyzer Common Fault Alarm | BOOL | READ | 00098 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Analyzer Control Cabinet
107.3 | 60-XA_400B | Stream_3_Model_Fault | Stream 3 - Analyzer Model Quality Fault | BOOL | READ | 00099 | N/A | N/A | N/A | N/A | OFF | FAULT | Calibration Quality
108.7 | 60-XA_400C | Stream_3_Sample_Panel_Fault | Stream 3-Sample Panel Common Fault Alarm | BOOL | READ | 00100 | N/A | N/A | N/A | N/A | OFF | FAULT | Faut Local To Sample System Enclosure
110.1 |  | SPARE | SPARE | BOOL | READ | 00101 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
111.5 |  | Stream_3_Temperature_Fault | Stream 3 - Temperature Transmitter Fault | BOOL | READ | 00102 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
112.9 |  | Stream_3_Pressure_Fault | Stream 3 - Pressure Transmitter Fault | BOOL | READ | 00103 | N/A | N/A | N/A | N/A | OFF | FAULT | Hardware Fault
114.3 |  | Stream_3_VCON_Normal | Stream 3 - Analyzer In Continous Analysis Mode | BOOL | READ | 00104 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
115.7 |  | Stream_3_VCON_Get_Ready | Stream 3 - Analyzer Sample Collection Mode Request | BOOL | READ | 00105 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
117.1 |  | Stream_3_VCON_Sampling | Stream 3 - Analyzer in Sample Collection Mode | BOOL | READ | 00106 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
118.5 |  | Stream_3_VCON_Ready | Stream 3 - Analyzer Ready For Sample Collection | BOOL | READ | 00107 | N/A | N/A | N/A | N/A | FALSE | TRUE | Local HMI status bit
119.9 |  | Stream_3_Sample_Source | Stream 3 - Sample Request Source | BOOL | READ | 00108 | N/A | N/A | N/A | N/A | HMI | SWITCH | Hardware Configuration Setting
121.3 |  | Stream_3_Active_Alarm | Stream 3 - Active Alarm | BOOL | READ | 00109 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
122.7 |  | Stream_3_Analyzer_Warning_Test_Enable | Stream 3 Analyzer Warning Test Enable | BOOL | READ | 00110 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
124.1 |  | Stream_3_Analyzer_Warning_Test | Stream 3 Analyzer Warning Test | BOOL | READ | 00111 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
125.5 |  | Stream_3_Analyzer_Fault_Test_Enable | Stream 3 Analyzer Fault Test Enable | BOOL | READ | 00112 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
126.9 |  | Stream_3_Analyzer_Fault_Test | Stream 3 Analyzer Fault Test | BOOL | READ | 00113 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
128.3 |  | Stream_3_Model_Warning_Test_Enable | Stream 3 Model Warning Test Enable | BOOL | READ | 00114 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
129.7 |  | Stream_3_Model_Warning_Test | Stream 3 Model Warning Test | BOOL | READ | 00115 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
131.1 |  | Stream_3_Model_Fault_Test_Enable | Stream 3 Model Fault Test Enable | BOOL | READ | 00116 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
132.5 |  | Stream_3_Model_Fault_Test | Stream 3 Model Fault Test | BOOL | READ | 00117 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
133.9 |  | Stream_3_Sample_Plan_Test_Enable | Stream 3 Sample Plan Test Enable | BOOL | READ | 00118 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
135.3 |  | Stream_3_Sample_Plan_Test | Stream 3 Sample Plan Test | BOOL | READ | 00119 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
136.7 |  | Stream_3_Transmission_Test_Enable | Stream 3 Transmission Test Enable | BOOL | READ | 00120 | N/A | N/A | N/A | N/A | OFF | ALARM | Local HMI status bit
138.1
139.5 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
140.9 | Holding Registers
142.3 | PLC_YEAR | PLC_YEAR | PLC Clock Year | INT | READ | 40001 |  | 2016 | 2116 |  |  |  | Real Time Clock From PLC
143.7 | PLC_MONTH | PLC_MONTH | PLC Clock Month | INT | READ | 40002 |  | 1 | 12 |  |  |  | Real Time Clock From PLC
145.1 | PLC_DAY | PLC_DAY | PLC Clock Day | INT | READ | 40003 |  | 1 | 31 |  |  |  | Real Time Clock From PLC
146.5 | PLC_HOUR | PLC_HOUR | PLC Clock Hour | INT | READ | 40004 |  | 0 | 24 |  |  |  | Real Time Clock From PLC
147.9 | PLC_MINUTE | PLC_MINUTE | PLC Clock Minute | INT | READ | 40005 |  | 0 | 60 |  |  |  | Real Time Clock From PLC
149.3 | PLC_SECOND | PLC_SECOND | PLC Clock Second | INT | READ | 40006 |  | 0 | 60 |  |  |  | Real Time Clock From PLC
150.7 | CT-4000 | CT_4000 | Communications Heartbeat Register to DCS | INT | READ | 40007 | N/A | 0 | 60 | N/A | N/A | N/A | PLC Clock Seconds passed onto master controller. Alarm if value has not changed after set time.
152.1 |  | STREAMS_ENABLED | Number of Streams Enabled in Logic | INT | READ | 40008 | N/A | 0 | 4 | N/A | N/A | N/A | Configuration Parameter
153.5
154.9 | STREAM - 1 - CONDENSATE
156.3 | 40-PIT-400 | Stream_1_Pressure | Stream 1, Pressure | REAL | READ | 40010 | N/A | 0 | 5000 | kPag | N/A | N/A
157.7 | 40-TIT-400 | Stream_1_Temperature | Stream 1, Temperature | REAL | READ | 40012 | N/A | -20 | 80 | C | N/A | N/A
159.1 | 40-AIT-400A | Stream_1_Deemed C4 | Stream 1, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40014 | N/A | 0 | 100 | VOL% | N/A | N/A
160.5 | 40-AIT-400A | Stream_1_C1 (Mol%) | Stream 1, C1 | REAL | READ | 40016 | N/A | 0 | 100 | MOL% | N/A | N/A
161.9 | 40-AIT-400B | Stream_1_C2 (Mol%) | Stream 1, C2 | REAL | READ | 40018 | N/A | 0 | 100 | MOL% | N/A | N/A
163.3 | 40-AIT-400C | Stream_1_C3 (Mol%) | Stream 1, C3 | REAL | READ | 40020 | N/A | 0 | 100 | MOL% | N/A | N/A
164.7 | 40-AIT-400D | Stream_1_iC4 (Mol%) | Stream 1, iC4 | REAL | READ | 40022 | N/A | 0 | 100 | MOL% | N/A | N/A
166.1 | 40-AIT-400E | Stream_1_nC4 (Mol%) | Stream 1, nC4 | REAL | READ | 40024 | N/A | 0 | 100 | MOL% | N/A | N/A
167.5 | 40-AIT-400J | Stream_1_Transmission | Stream 1, Transmission | REAL | READ | 40026 | N/A | 0 | 100 | % | N/A | N/A
168.9 |  | Stream_1_Sample_Mode | Stream 1, Sampling Mode | INT | READ | 40028 | N/A | 0 | 4 | N/A | N/A | N/A
170.3 |  | Stream_1_Sample_Mode_HMI_Select | Stream 1, Sampling Mode HMI Select | INT | READ | 40029 | N/A | 0 | 1 | N/A | N/A | N/A
171.7 |  | Stream_1_Pressure_Range_Lo | Stream 1, Cell Pressure Scale Low SP | REAL | READ | 40030 | N/A | 0 | 100 | kPag | N/A | N/A
173.1 |  | Stream_1_Pressure_Range_Hi | Stream 1, Cell Pressure Scale High SP | REAL | READ | 40032 | N/A | 0 | 100 | kPag | N/A | N/A
174.5 |  | Stream_1_Pressure_Alarm_Hi_SP | Stream 1, Cell Pressure Scale High Alarm SP | REAL | READ | 40034 | N/A | 0 | 100 | kPag | N/A | N/A
175.9 |  | Stream_1_Temperature_Range_Lo | Stream 1, Cell Temperature Scale Low SP | REAL | READ | 40036 | N/A | 0 | 300 | C | N/A | N/A
177.3 |  | Stream_1_Temperature_Range_Hi | Stream 1, Cell Temperature Scale High SP | REAL | READ | 40038 | N/A | 0 | 300 | C | N/A | N/A
178.7 |  | Stream_1_Temperature_Alarm_Hi_SP | Stream 1, Cell Temperature Scale High Alarm SP | REAL | READ | 40040 | N/A | 0 | 300 | C | N/A | N/A | Analyzer Diagnostic Signal
180.1 |  | Stream_1_Transmission_Test | Stream 1 Transmission Test | REAL | R/W | 40042 | N/A | 0 | 300 | % | N/A | N/A
181.5
182.9 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
184.3 | STREAM - 2 - CONDENSATE
185.7 | 50-PIT-400 | Stream_2_Pressure_1 | Stream 2, Pressure | REAL | READ | 40060 | N/A | 0 | 2000 | kPag | N/A | N/A
187.1 | 50-TIT-400 | Stream_2_Temperature_1 | Stream 2, Temperature | REAL | READ | 40062 | N/A | -20 | 80 | C | N/A | N/A
188.5 | 50-AIT-400A | Stream_2_Deemed C4 | Stream 2, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40064 | N/A | 0 | 100 | VOL% | N/A | N/A
189.9 | 50-AIT-400C | Stream_2_C1 (Vol%) | Stream 2, C1 | REAL | READ | 40066 | N/A | 0 | 100 | VOL% | N/A | N/A
191.3 | 50-AIT-400D | Stream_2_C2 (Vol%) | Stream 2, C2 | REAL | READ | 40068 | N/A | 0 | 100 | VOL% | N/A | N/A
192.7 | 50-AIT-400E | Stream_2_C3 (Vol%) | Stream 2, C3 | REAL | READ | 40070 | N/A | 0 | 100 | VOL% | N/A | N/A
194.1 | 50-AIT-400F | Stream_2_iC4 (Vol%) | Stream 2, iC4 | REAL | READ | 40072 | N/A | 0 | 100 | VOL% | N/A | N/A
195.5 | 50-AIT-400G | Stream_2_nC4 (Vol%) | Stream 2, nC4 | REAL | READ | 40074 | N/A | 0 | 100 | VOL% | N/A | N/A
196.9 | 50-AIT-400H | Stream_2_Stream_2_Transmission | Stream 2, Transmission | REAL | READ | 40076 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal
198.3 |  | Stream_2_Sample_Mode | Stream 2, Sampling Mode | INT | READ | 40078 | N/A | 0 | 3 | N/A | N/A | N/A | 0=Normal, 1=Get Ready, 2=Ready, 3=Sampling
199.7 |  | Stream_2_Sample_Mode_HMI_Select | Stream 2, Sampling Mode HMI Select | INT | R/W | 40079 | N/A | 0 | 2 | N/A | N/A | N/A | 1 = HMI P2, 2 = HMI P3
201.1 |  | Stream_2_Pressure_Range_Lo | Stream 2, Cell Pressure Scale Low SP | REAL | R/W | 40080 | N/A | 0 | 10000 | kpa | N/A | N/A
202.5 |  | Stream_2_Pressure_Range_Hi | Stream 2, Cell Pressure Scale High SP | REAL | R/W | 40082 | N/A | 0 | 10000 | kpa | N/A | N/A
203.9 |  | Stream_2_Pressure_Alarm_Hi_SP | Stream 2, Cell Pressure Scale High Alarm SP | REAL | R/W | 40084 | N/A | 0 | 10000 | kpa | N/A | N/A
205.3 |  | Stream_2_Temperature_Range_Lo | Stream 2, Cell Temperature Scale Low SP | REAL | R/W | 40086 | N/A | 0 | 300 | C | N/A | N/A
206.7 |  | Stream_2_Temperature_Range_Hi | Stream 2, Cell Temperature Scale High SP | REAL | R/W | 40088 | N/A | 0 | 300 | C | N/A | N/A
208.1 |  | Stream_2_Temperature_Alarm_Hi_SP | Stream 2, Cell Temperature Scale High Alarm SP | REAL | R/W | 40090 | N/A | 0 | 300 | C | N/A | N/A
209.5 |  | Stream_2_Transmission_Test | Stream 2 Transmission Test | REAL | R/W | 40092 | N/A | 0 | 100 | % | N/A | N/A
210.9
212.3 | Tag Number | PLC Tag | Service Description (Max=32 Characters) | Data Type | Read/Write | PLC ModBus Address | Bit | Min Range | Max Range | Eng Unit | STATUS 0 | STATUS 1 | Comments | CHECKED BY
213.7 | STREAM - 3 - CONDENSATE
215.1 | 60-PIT-400 | Stream_3_Pressure_1 | Stream 3, Pressure | REAL | READ | 40110 | N/A | 0 | 2000 | kPag | N/A | N/A
216.5 | 60-TIT-400 | Stream_3_Temperature_1 | Stream 3, Temperature | REAL | READ | 40112 | N/A | -20 | 80 | C | N/A | N/A
217.9 | 60-AIT-400A | Stream_3_Deemed C4 | Stream 3, Deemed C4- calculated as: Deemed C4- = (3*(%C1+%C2+%C3)) + (%iC4+%nC4) | REAL | READ | 40114 | N/A | 0 | 100 | VOL% | N/A | N/A
219.3 | 60-AIT-400C | Stream_3_C1 (Vol%) | Stream 3, C1 | REAL | READ | 40116 | N/A | 0 | 100 | VOL% | N/A | N/A
220.7 | 60-AIT-400D | Stream_3_C2 (Vol%) | Stream 3, C2 | REAL | READ | 40118 | N/A | 0 | 100 | VOL% | N/A | N/A
222.1 | 60-AIT-400E | Stream_3_C3 (Vol%) | Stream 3, C3 | REAL | READ | 40120 | N/A | 0 | 100 | VOL% | N/A | N/A
223.5 | 60-AIT-400F | Stream_3_iC4 (Vol%) | Stream 3, iC4 | REAL | READ | 40122 | N/A | 0 | 100 | VOL% | N/A | N/A
224.9 | 60-AIT-400G | Stream_3_nC4 (Vol%) | Stream 3, nC4 | REAL | READ | 40124 | N/A | 0 | 100 | VOL% | N/A | N/A
226.3 | 60-AIT-400H | Stream_3_Stream_3_Transmission | Stream 3, Transmission | REAL | READ | 40126 | N/A | 0 | 100 | % | N/A | N/A | Analyzer Diagnostic Signal
227.7 |  | Stream_3_Sample_Mode | Stream 3, Sampling Mode | INT | READ | 40128 | N/A | 0 | 3 | N/A | N/A | N/A | 0=Normal, 1=Get Ready, 2=Ready, 3=Sampling
229.1 |  | Stream_3_Sample_Mode_HMI_Select | Stream 3, Sampling Mode HMI Select | INT | R/W | 40129 | N/A | 0 | 2 | N/A | N/A | N/A | 1 = HMI P2, 2 = HMI P3
230.5 |  | Stream_3_Pressure_Range_Lo | Stream 3, Cell Pressure Scale Low SP | REAL | R/W | 40130 | N/A | 0 | 10000 | kpa | N/A | N/A
231.9 |  | Stream_3_Pressure_Range_Hi | Stream 3, Cell Pressure Scale High SP | REAL | R/W | 40132 | N/A | 0 | 10000 | kpa | N/A | N/A
233.3 |  | Stream_3_Pressure_Alarm_Hi_SP | Stream 3, Cell Pressure Scale High Alarm SP | REAL | R/W | 40134 | N/A | 0 | 10000 | kpa | N/A | N/A
234.7 |  | Stream_3_Temperature_Range_Lo | Stream 3, Cell Temperature Scale Low SP | REAL | R/W | 40136 | N/A | 0 | 300 | C | N/A | N/A
236.1 |  | Stream_3_Temperature_Range_Hi | Stream 3, Cell Temperature Scale High SP | REAL | R/W | 40138 | N/A | 0 | 300 | C | N/A | N/A
237.5 |  | Stream_3_Temperature_Alarm_Hi_SP | Stream 3, Cell Temperature Scale High Alarm SP | REAL | R/W | 40140 | N/A | 0 | 300 | C | N/A | N/A
238.9 |  | Stream_3_Transmission_Test | Stream 3 Transmission Test | REAL | R/W | 40142 | N/A | 0 | 100 | % | N/A | N/A
240.3

## CONDY A1
40-AIT-400
SPECIES | REG TYPE | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1_MOL | Input | 7001 | 8001 | 32-bit Floating Point | VOL%
C2_MOL | Input | 7003 | 8003 | 32-bit Floating Point | VOL%
C3_MOL | Input | 7005 | 8005 | 32-bit Floating Point | VOL%
iC4_MOL | Input | 7007 | 8007 | 32-bit Floating Point | VOL%
nC4_MOL | Input | 7009 | 8009 | 32-bit Floating Point | VOL%
DEEMED C4 | Input | 7011 | 8011 | 32-bit Floating Point | VOL%
Transmission_1 | Input | 7017 |  | 32-bit Floating Point | %
Fault_Ireg | Input | 7019 |  | 16-bit Integer | ENCODED
Warning_Ireg | Input | 7020 |  | 16-bit Integer | ENCODED
Flow Interrupt | Input | 7021 |  | 16-bit Integer | 41=Closed
Alarm IReg | Input | 7022 |  | 16-bit Integer | 0=Open, 41 = Closed
Model IReg | Input | 7023 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7024 |  | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7025 |  | 16-bit Integer | 41=Trigger to pull sample
INPUTS
Temperature_1 | Holding | 1 | N/A | 16-bit Integer
Pressure_1 | Holding | 2 | N/A | 16-bit Integer
vcon trigger | Holding | 3 | N/A | 16-bit Integer
no flow | Holding | 4 | N/A | 16-bit Integer
vcon_get_ready | Holding | 21 | N/A | 16-bit Integer | 41=VCON GET READY
vcon_sample | Holding | 22 | N/A | 16-bit Integer | 41=SAMPLE IN PROGRESS
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer | REMOTE POWER CYCLE
Status_Modbus | Input | 7097 | N/A | 16-bit Integer | STREAM INDICATOR
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer | TOGGLE BETWENN 0 AND 41
prefix:

## CONDY A2
50-AIT-400
SPECIES | REG TYPE | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1_VOL | Input | 7101 | 8101 | 32-bit Floating Point | VOL%
C2_VOL | Input | 7103 | 8103 | 32-bit Floating Point | VOL%
C3_VOL | Input | 7105 | 8105 | 32-bit Floating Point | VOL%
iC4_VOL | Input | 7107 | 8107 | 32-bit Floating Point | VOL%
nC4_VOL | Input | 7109 | 8109 | 32-bit Floating Point | VOL%
DEEMED_C4 | Input | 7111 | 8111 | 32-bit Floating Point | VOL%
Transmission_1 | Input | 7117 |  | 32-bit Floating Point | %
Fault_Ireg | Input | 7119 |  | 16-bit Integer | ENCODED
Warning_Ireg | Input | 7120 |  | 16-bit Integer | ENCODED
Flow Interrupt | Input | 7121 |  | 16-bit Integer | 41=Closed
Alarm IReg | Input | 7122 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
Model IReg | Input | 7123 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7124 |  | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7125 |  | 16-bit Integer | 41=Trigger to pull sample
INPUTS
Temperature_1 | Holding | 5 | N/A | 16-bit Integer
Pressure_1 | Holding | 6 | N/A | 16-bit Integer
vcon trigger | Holding | 7 | N/A | 16-bit Integer
no flow | Holding | 8 | N/A | 16-bit Integer
vcon_get_ready | Holding | 23 | N/A | 16-bit Integer | 41=VCON GET READY
vcon_sample | Holding | 24 | N/A | 16-bit Integer | 41=SAMPLE IN PROGRESS
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer | REMOTE POWER CYCLE
Status_Modbus | Input | 7097 | N/A | 16-bit Integer | STREAM INDICATOR
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer | TOGGLE BETWENN 0 AND 41

## CONDY A3
60-AIT-400
SPECIES | REG TYPE | Reg # | 24_Hr_Avg Reg# | Data Type | Range/Logic
C1_VOL | Input | 7201 | 8201 | 32-bit Floating Point | VOL%
C2_VOL | Input | 7203 | 8203 | 32-bit Floating Point | VOL%
C3_VOL | Input | 7205 | 8205 | 32-bit Floating Point | VOL%
iC4_VOL | Input | 7207 | 8207 | 32-bit Floating Point | VOL%
nC4_VOL | Input | 7209 | 8209 | 32-bit Floating Point | VOL%
DEEMED_C4 | Input | 7211 | 8211 | 32-bit Floating Point | VOL%
Transmission_1 | Input | 7217 |  | 32-bit Floating Point | %
Fault_Ireg | Input | 7219 |  | 16-bit Integer | ENCODED
Warning_Ireg | Input | 7220 |  | 16-bit Integer | ENCODED
Flow Interrupt | Input | 7221 |  | 16-bit Integer | 41=Closed
Alarm IReg | Input | 7222 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
Model IReg | Input | 7223 |  | 16-bit Integer | 0=Normal, 1=Warning, 2=Fault
VCON IReg | Input | 7224 |  | 16-bit Integer | 41=VCON_Ready
Sample Plan IReg | Input | 7225 |  | 16-bit Integer | 41=Trigger to pull sample
INPUTS
Temperature_1 | Holding | 9 | N/A | 16-bit Integer
Pressure_1 | Holding | 10 | N/A | 16-bit Integer
vcon trigger | Holding | 11 | N/A | 16-bit Integer
no flow | Holding | 12 | N/A | 16-bit Integer
vcon_get_ready | Holding | 25 | N/A | 16-bit Integer | 41=VCON GET READY
vcon_sample | Holding | 26 | N/A | 16-bit Integer | 41=SAMPLE IN PROGRESS
CONFIG SETTINGS
spec_power | Input | 7095 | N/A | 16-bit Integer | REMOTE POWER CYCLE
Status_Modbus | Input | 7097 | N/A | 16-bit Integer | STREAM INDICATOR
Beat_Modbus | Input | 7098 | N/A | 16-bit Integer | TOGGLE BETWENN 0 AND 41

## CHANGE LOG
DATE | CHANGES | BY
2020-12-08 | INITIAL DRAFT | DD

## DataTypes (hidden)
Data Type | Description
BOOL | Boolean, Single bit
WORD | Unsigned 16 bit value bit 0 is the low bit bit 15 is the high bit
SHORT | Signed 16 bit value bit 0 is the low bit bit 14 is the high bit bit 15 is the sign bit
DWORD | Unsigned 32 bit value bit 0 is the low bit bit 31 is the high bit
LONG | Signed 32 bit value bit 0 is the low bit bit 30 is the high bit bit 31 is the sign bit
BCD | Two byte packed BCD Value range is 0-9999. Behavior is undefined for values beyond this range.
LBCD | Four byte packed BCD Value range is 0-99999999. Behavior is undefined for values beyond this range.
STRING | Null terminated ASCII string Supported on Modbus Model, includes Hi-Lo Lo-Hi byte order selection.
DOUBLE (Note 1) | 64 bit floating point value The driver interprets four consecutive registers as a double precision value by making the last two registers the high DWord and the first two registers the low DWord.
DOUBLE Example | If register 40001 is specified as a double, bit 0 of register 40001 would be bit 0 of the 64 bit data type and bit 15 of register 40004 would be bit 63 of the 64 bit data type.
FLOAT (Note 1) | 32 bit floating point value The driver interprets two consecutive registers as a single precision value by making the last register the high word and the first register the low word.
FLOAT Example | If register 40001 is specified as a float, bit 0 of register 40001 would be bit 0 of the 32 bit data type and bit 15 of register 40002 would be bit 31 of the 32 bit data type.
Notes:
1. The descriptions assume the default; that is, first DWord low data handling of 64 bit data types and first word
low data handling of 32 bit data types.
2. Standard data format names have been selected. If other names are desired, specify the bytes and range.